Army Reserve Enterprise Building Control System (EBCS)

Design Guide

Updated Revision: October 2021

Table of Contents

List of Acronyms	1

Revision History	2

1.0	Introduction	3

1.1.	EBCS System Architecture	3

2.0	Technical Design Guide	4

2.1	Hardware	4

2.2   Steps for Integration	4

2.2.1	Installing JACE	4

2.2.2	JACE Setup and Configuration	4

2.2.3	JACE Programming	5

2.2.4	Graphical User Interface (GUI)	6

2.2.5	Final Steps	7

Attachment A.  Unified Facilities Guide Specifications	8

Attachment B.  Integration Ready Definition	8

Attachment C.  Site Readiness Assessment	8

Attachment D.  DHCP Reservation	8

Attachment E.  JACE Enclosure Layout	9

Attachment F.  User Profiles	9

Attachment G.  Point Naming Convention	9

Attachment H. MDMS Standard Meter Data Format	9

Attachment I. EBCS User Interface Examples	9

Attachment J.  QA/QC Checklist	9

# List of Acronyms

ARNET: Army Reserve Network.

BCS: Building Control System

DHCP: Dynamic Host Configuration Protocol

EBCS: Enterprise Building Control System

FAC: Facility

FOXS: Secured communications protocol developed as part of the Tridium Niagara framework

GUI: Graphical User Interface

HTTPS: Hypertext Transfer Protocol Secure

HVAC: Heating, Ventilation, and Air Conditioning

IC: Integration Controller

IP: Internet Protocol

JACE: Java Application Control Engine

JAR: Niagara software operations modules

MAC: Media Access Control

NAC: Network Area Controller

NEMA: National Electrical Manufactures Association

POC: Point of Contact

QA/QC: Quality Assurance / Quality Check

QNX: Operation system

RD: Readiness Division

SRA: Site Readiness Assessment

TCP: Transmission Control Protocol

TLS: Transport Layer Security

UFGS: Unified Facilities Guide Specifications

UL: Underwriters Laboratories

WIFI: Wireless network

# Revision History

| Version | Description | Date |
| --- | --- | --- |
| January 2021 | Initial Version | JAN 2021 |
| October 2021 | Design Guide: Specs updated to (1) include point naming convention for meters; (2) requiring the integrator to send trend data to the SQL server Attachment C: Updated per FY21 SRAs Attachment H: New attachment (MDMS Standard Meter Data Format) Attachment J: (1) Removed “Logic/Sequencing” from Graphics section; (2) Updated “Logic/Sequencing” verbiage on Line 65; (3) Added “JACE Model and Niagara Version” to Line 72 | OCT 2021 |

# Introduction

The Enterprise Building Control System (EBCS) Technical Design Guide provides the technical details for both EBCS equipment and hardware; and the system configuration. This guide follows and is supplemental to the standards of UFGS 23.09.00 and UFGS 25.10.10 found in Attachment A.

## EBCS System Architecture

The EBCS architecture relies on the Tridium Niagara 4 Framework to provide seamless integration of common and accepted hardware at the building level to communicate with a central server at the “enterprise” level.  The Java Application Control Engine (JACE) is the device that provides a firewall to allow local building controls from various vendors to connect to and communicate across the ARNET (see Figure 1).

Figure 1.  EBCS Simplified Architecture

The NAC/JACE example in Figure 1 shows building equipment (e.g., chillers, air-handlers, etc.) connected to a proprietary vender’s device called a Network Area Controller (NAC).  The NAC cannot be connected to the ARNET directly.  Therefore, an Integration Controller (IC) JACE serves as a gateway to make the data and control function of the local BCS/NAC available across the network. Sometimes the NAC is also a JACE but dedicated to building-level functions only, thus resulting in a JACE/JACE configuration.  Lastly, the JACE/Server configuration uses a single JACE as both the NAC and IC, although users should be careful that these functions do not over-whelm the capabilities of the JACE. This configuration will be determined by the RD with support from the integration contractor.

# Technical Design Guide

This guidance provides a framework for systems that are NAC/JACE, JACE/JACE, and JACE/Server configurations. Integration configuration shall be determined by each Readiness Division (RD). The determination of these configurations relies not only on technical capabilities, but also contractual parameters. Hardware and system responsibilities must be taken into consideration while evaluating the integration configurations.

A BCS is considered “Integration Ready” when the system does not require any additional work before establishing a connection and integrating to the EBCS server. Review Attachment B to determine when the system is integration ready. The primary integration steps are: determining the integration configuration and verifying the JACE, establishing communications between the JACE and the EBCS server, and establishing links to all the points in the existing system.

## Hardware

The IC JACE must meet the following specifications regardless of the integration configuration.

- VYKON JACE 8000 series with an open license. License version must be 4.7 or newer with the Wi-Fi disabled.

- 5 year SMA maintenance plan

- License should include the workbench tools to be installed on the JACE.

- A dedicated UL-listed, Class 2, 24Vac power supply with a manufacture approved surge protection. The JACE must be powered by a dedicated breaker or off the circuit providing power to the local BCS NAC (if existing).

- Mounted in a NEMA Type III enclosure with associated wiring, fusing, and mounting blocks.

## 2.2   Steps for Integration

- Prior to integration, a Site Readiness Assessment (SRA) must be performed by the contractor on all facilities appropriate for integration at that site. The RD POC will provide guidance to the contractor on which facilities require a SRA. The SRA can be found in Attachment C.

## Installing JACE

- The JACE MAC address, serial number, QNX code, and additional information must be entered in the “Request for DHCP Reservation Form” in Attachment D and submitted to the RD POC and ARIMD EBCS Sustainability Manager for DHCP reservation.

- Integration contractor shall work with the RD POC to determine the ideal location of the JACE.

- The contractor shall connect the JACE to the local BCS NAC (if existing) and provide all Cat 6E cabling to the ARNET switch.

- Any onsite BCS computers inside the building used for control or monitoring need to be connected on the Port 2 side of the JACE and remain operational.

- Label JACE with station name and Port 1 and Port 2 MAC address

- Review Attachment E for a JACE enclosure layout for further technical installation guidance.

## JACE Setup and Configuration

- A Cat 6E cable must be plugged into Comm 1 of the JACE from the ARNET switch.

- Only the following runtime profiles shall be enabled.

  - RUNTIME: Module JARs having core runtime Java classes only, no user interface.

  - UX: Module JARs having lightweight HTML5+JavaScript+CSS user interface only.

  - WB: Module JARs having Workbench or Workbench Applet user interface classes.

- The contractor will use a standardized station name and hostname that will be provided by the RD POC. Station name and hostname will adhere to the following format.

  - HVAC Controls Station Name: FACID_FACNUM_C01

  - MDMS Station Name: FACID_FACNUM_M01

- A station template will be provided by the RD POC that must be used by the contractor.

- All communications between Niagara devices and the EBCS server will be secured with SSL, using the following points.

| Interface | Protocol | Specified Port |
| --- | --- | --- |
| Internet Browser | HTTPS | 443 |
| Niagara Station | FOXS | 4911 |
| Niagara Station | TLSv1 | 5011 |

- When configuring the JACE in the TCP/IP configuration screen, Comm 1 will be set for DHCPv4 enabled. DHCPv6 will be disabled. Configure Hostname to match station name.

  - HVAC Controls Hostname: FACID-FACNUM-C01

  - MDMS Hostname: FACID-FACNUM-M01

- When configuring the Jace in the TCP/IP config screen, Comm 2 on the JACE will be configured with a standardized static IP address and subnet mask to allow for a local laptop to be connected for future onsite work.

- The contractor will refer to the document titled “User Profiles” (Attachment F) for configuration of user name and password combinations and system passphrases.

## JACE Programming

- The contractor will use a standardized point naming convention in the JACE for all data points as listed in “Point Naming Convention” in Attachment G for HVAC and auxiliary equipment.

- The contractor will use a standardized point naming convention for meter points in accordance with the MDMS Variable from Table 1 in Attachment H.

- The contractor will add alarm extensions to the data points as designated in the “Point Naming Convention”. Alarm messages will be added to each alarm as outlined below.

  - Out of Range (Analog Points). The message will display the current value of the point and either the high or low threshold.

  - Command Failure (Boolean Point). The message will display the current command of the point and the current status.

  - Change of Value (Boolean or Enumerated Points). The message will display the current value of the point.

  - Change of Status (Niagara Components). The message will display the current value of the component.

- The contractor will add trend extensions to the data points as designated in the “Point Naming Convention Guide”. The data types that will be used for the trend extension are outlined below.

  - Interval Trends. This trend type will be assigned to analog points that are fast changing in nature. The trend extension will be configured to record a data point every 5-15 minutes.

  - Change-of-Value Trends. This trend type will be assigned to either analog or Boolean points that are not fast changing in nature. The trend extension will automatically be configured to record a data point whenever there is a change of value in the point.

- The trend extension configuration will be set to allow for a minimum three-day rolling window of data, but not to exceed 1800 records per JACE.

- Trend extensions must be added to the Rdbms Network to be exported to the EBCS SQL Server.

  - Trend extensions must be added to the Rdbms Network station in accordance to the associated Army Reserve Division and controller type. For example, BCS trend extensions for a building in the 63rd DIV will be added to the “63RD_EBCS” station.

  - A New Folder must be created for the new trend extensions in the Rdbms Network station for data organization purposes.

  - Trend extensions added to any of the “_MDMS” Rdbms Network stations must be configured to export hourly for all seven days of the week starting at 12:00 A.M. EST.

  - Trend extensions added to any of the “_EBCS” Rdbms Network stations must be configured to export as follows:

    - 63RD: Daily at 1:20 A.M. EST for all seven days of the week

    - 81RD: Daily at 2:20 A.M. EST for all seven days of the week

    - 88RD: Daily at 4:20 A.M. EST for all seven days of the week

    - 99RD: Daily at 3:20 A.M. EST for all seven days of the week

## Graphical User Interface (GUI)

- A station template will be provided by the RD POC that contains the GUI package that must be used by the contractor.

- The GUI package will provide template graphics for system and equipment level screens, layout, and functionality. Attachment I provides examples of the graphics.

- The contractor will edit the equipment level screens to be representative of the equipment configuration and piping/ducting layout.

- Floorplans will be provided by the RD POC will be added to the floorplan graphics by the contractor.

  - The contractor will implement a floorplan color presentation to match each zone as served by the HVAC system. The floorplans in the template station can be used as an example.

  - The contractor will implement a zone temperature deviation calculation for each zone and integrate the deviation into the floorplans. The deviation scale will be setup as followed. The floorplans in the template station can be used as an example.

Green: when zone is +/- 2°F of setpoint

Yellow: when zone is above setpoint by 2-4°F

Orange: when zone is above setpoint by 4-6°F

Red: when zone is above setpoint by more than 6°F

Light blue: when zone is below setpoint by 2-4°F

Blue: when zone is below setpoint by 4-6°F

Dark blue: when zone is below setpoint by more than 6°F

- Contractor shall install all building graphics on the JACE. If the JACE was login into at the building the graphics from the building down to the equipment should look the same as the server level graphics.

## Final Steps

- The contractor will work with the RD POC to test and verify the access and basic functionality of the new JACE is satisfactory while accessing the system remotely.

- The contractor will provide the following to verify quality workmanship.

  - Use hole-knockout protectors, properly aligned holes, and do not leave any jagged edges.

  - Submit photos of before and after JACE installation including close up images of the cable connections at the JACE and at the local BCS (if existing), cable pathways, and all enclosure penetrations.

  - Completed QA/QC checklist found in Attachment J.

  - Red-lines of building layouts and equipment manuals/documentation in Microsoft Office format.

# Attachment A.  Unified Facilities Guide Specifications

The EBCS framework and all underlaying BCS must be in accordance to the Unified Facilities Guide Specification (UFGS) from the Department of Defense. Below are the links for the full versions of the applicable specification. Amended examples are in Attachment A.

UFGS 23 09 00: Instrumentation and Control for HVAC

http://www.wbdg.org/ffc/dod/unified-facilities-guide-specifications-ufgs/ufgs-23-09-00

UFGS 25 10 10: Utility Monitoring and Control System (UMCS) Front End and Integration

http://www.wbdg.org/ffc/dod/unified-facilities-guide-specifications-ufgs/ufgs-25-10-10

# Attachment B.  Integration Ready Definition

Attachment B provides the definition of systems that are considered “Integration Ready”. A BCS is considered Integration Ready if it meets all the critical criteria without needing additional work.

# Attachment C.  Site Readiness Assessment

Attachment C is the SRA workbook that must be completed before any system is integrated to the EBCS. The primary functions of the SRA are to:

- Gather details about the current BCS (vendor, software, IP, etc)

- Perform functional testing on the BCS in relation to the integrated mechanical equipment

- Determine if the BCS is Integration Ready

- Complete an onsite checklist on BCS, HVAC, networking, and metering details

- Draft preliminary list of expected costs

# Attachment D.  DHCP Reservation

Attachment D is the form that can be used for submitting DHCP and IP reservations and assist RD’s with technical documentation. The form includes the following fields:

- FAC ID and Building

- Panel Name

- Tridium Jace Model

- MAC Address Port 1 & 2

- Serial Number

- QNX Code

- Station Passphrase

- Host ID#

- Platform Username & Password

- Station Admin Username &Password

- DHCP Reservation

- Port 1 & 2 DHCP IP Address

- Port 1 & 2 DHCP Subnet Mask

# Attachment E.  JACE Enclosure Layout

Attachment E provides schematics for potential parts list and JACE wiring diagrams.

# Attachment F.  User Profiles

Attachment F is the user profile sheet detailing the specifications for credentials, roles, and accessibility for each user. These will be defined by each RD and will be specific to the needs of each RD.

# Attachment G.  Point Naming Convention

Attachment G provides the naming conventions for control points.  Additionally, this table indicates which points should be trending (storing data histories) and which should be generating alarms on faults.

# Attachment H. MDMS Standard Meter Data Format

Attachment H is the MDMS Standard Meter Data Format to provide the guidance for which MDMS metering data points must be named when they are integrated to EBCS.

# Attachment I. EBCS User Interface Examples

Attachment I provides examples of the user interface. Exact images are subject to change, so the images are to provide a general understanding. An RD-provided station template will be used that contains the required graphics package.

# Attachment J.  QA/QC Checklist

Attachment J is the QA/QC checklist to be completed after EBCS integration is complete.