**************************************************************************

THIS IS A DRAFT DOCUMENT EDITED BY PNNL TO

- EXCLUDE ANY SPECS IN REGARDS TO LON/LONWORKS

- ADD SPECS RELATED TO THE EBCS

DOCUMENT IS CURRENTLY FOR REFERENCE ONLY AND SHALL NOT BE USED FOR SOLICITATION OR PROJECT DEVELOPMENT.

**************************************************************************

USACE / NAVFAC / AFCEC / NASA UFGS-25 05 11 (November 2017)

------------------------------------

Preparing Activity: USACE

UNIFIED FACILITIES GUIDE SPECIFICATIONS

References are in agreement with UMRL dated July 2019

**************************************************************************

SECTION TABLE OF CONTENTS

DIVISION 25 - INTEGRATED AUTOMATION

SECTION 25 05 11

CYBERSECURITY FOR FACILITY-RELATED CONTROL SYSTEMS

11/17

PART 1 GENERAL

1.1 CONTROL SYSTEM APPLICABILITY

1.2 RELATED REQUIREMENTS

1.3 REFERENCES

1.4 DEFINITIONS

1.4.1 Computer

1.4.2 Network Connected

1.4.3 User Account Support Levels

1.4.3.1 FULLY Supported

1.4.3.2 MINIMALLY Supported

1.4.3.3 NOT Supported

1.4.4 User Interface

1.4.4.1 Limited Local User Interface

1.4.4.2 Full Local User Interface

1.4.4.3 Remote User Interface

1.5 ADMINISTRATIVE REQUIREMENTS

1.5.1 Coordination

1.6 SUBMITTALS

1.7 QUALITY CONTROL

1.7.1 Regulatory Requirements

1.7.2 [Certifications][Qualifications]

1.7.3 Pre-Construction Testing

1.8 DELIVERY, STORAGE, AND HANDLING

1.9 CYBERSECURITY DOCUMENTATION

1.9.1 Cybersecurity Interconnection Schedule

1.9.2 Network Communication Report

1.9.3 Control System Inventory Report

1.9.4 Software Recovery and Reconstitution Images

1.9.5 Cybersecurity Riser Diagram

1.9.6 Control System Cybersecurity Documentation

1.9.6.1 Software Applications

1.9.6.2 For HVAC Control System Devices

1.9.6.2.1 HVAC Control System Devices FULLY Supporting User

Accounts

1.9.6.2.2 All Other HVAC Control System Devices

1.9.6.3 [_____] Control System Devices

1.9.6.4 Default Requirements for Control System Devices

1.10 SOFTWARE UPDATE LICENSING

1.11 CYBERSECURITY DURING CONSTRUCTION

1.11.1 Contractor Computer Equipment

1.11.1.1 Operating System

1.11.1.2 Anti-Malware Software

1.11.1.3 Passwords and Passphrases

1.11.1.4 Contractor Computer Cybersecurity Compliance Statements

1.11.2 Temporary IP Networks

1.11.2.1 Network Boundaries and Connections

1.11.3 Government Access to Network

1.11.4 Temporary Wireless IP Networks

1.11.5 Passwords and Passphrases

1.11.6 Contractor Temporary Network Cybersecurity Compliance

Statements

1.12 CYBERSECURITY DURING WARRANTY PERIOD

PART 2 PRODUCTS

PART 3 EXECUTION

3.1 ACCESS CONTROL REQUIREMENTS

3.1.1 User Accounts

3.1.1.1 Computers

3.1.1.2 For HVAC Control System Devices

3.1.1.3 [_____] Control System Devices

3.1.1.4 Default Requirements for Control System Devices

3.1.2 Unsuccessful Logon Attempts

3.1.2.1 Devices MINIMALLY Supporting Accounts

3.1.2.2 Devices FULLY Supporting Accounts

3.1.2.3 High Availability Interfaces Exempt from Unsuccessful

Logon Attempts Requirements

3.1.3 System Use Notification

3.1.3.1 User Interface Banner Schedule

3.1.4 Permitted Actions Without Identification or Authentication

3.2 CYBERSECURITY AUDITING

3.2.1 Audit Events, Content of Audit Records, and Audit Generation

3.2.1.1 Computers

3.2.1.1.1 Audited Events

3.2.1.1.2 Audit Event Information To Record

3.2.1.2 For HVAC Control System Devices

3.2.1.2.1 HVAC Control System Devices FULLY Supporting User

Accounts

3.2.1.2.2 Other HVAC Control System Devices

3.2.1.3 [_____] Control System Devices

3.2.1.4 Default Requirements for Control System Devices

3.2.1.4.1 Devices Which FULLY Support Accounts

3.2.1.4.1.1 Audited Events

3.2.1.4.1.2 Audit Event Information To Record

3.2.1.4.2 Devices Which Do Not FULLY Support Accounts

3.2.2 Audit Storage Capacity and Audit Upload

3.2.2.1 Device Audit Record Upload Software

3.2.3 Response to Audit Processing Failures

3.2.4 Time Stamps

3.2.4.1 Computers

3.2.4.2 For HVAC Control System Devices

3.2.4.3 [_____] Control System Devices

3.2.4.4 Default Requirements for Control System Devices

3.3 REQUIREMENTS FOR LEAST FUNCTIONALITY

3.3.1 Non-IP Control Networks

3.3.2 IP Control Networks

3.4 SAFE MODE AND FAIL SAFE OPERATION

3.5 IDENTIFICATION AND AUTHENTICATION

3.5.1 User Identification and Authentication

3.5.1.1 HVAC Control Systems Devices

3.5.1.2 Electronic Security System Devices

3.5.1.3 [_____] Control System Devices

3.5.1.4 Default Requirements for Control System Devices

3.5.2 Authenticator Management

3.5.2.1 Authentication Type

3.5.2.1.1 For HVAC Control System Devices

3.5.2.1.2 [_____] Control System Devices

3.5.2.1.3 Default Requirements for Control System Devices

3.5.2.2 Password-Based Authentication Requirements

3.5.2.2.1 Passwords for Computers

3.5.2.2.2 Passwords for Non-Computer Devices FULLY Supporting

Accounts

3.5.2.2.3 Passwords for Web Interfaces

3.5.2.2.4 Passwords for Devices Minimally Supporting Accounts

3.5.2.2.5 Password Configuration and Reporting

3.5.2.3 Hardware Token-Based Authentication Requirements

3.5.3 Authenticator Feedback

3.5.4 Device Identification and Authentication

3.5.4.1 For HVAC Control System Devices

3.5.4.2 [_____] Control System Devices

3.5.4.3 Default Requirements for Control System Devices

3.5.5 Cryptographic Module Authentication

3.6 EMERGENCY POWER

3.7 DURABILITY TO VULNERABILITY SCANNING

3.7.1 HVAC Control System Devices Other Than Computers

3.7.2 [_____] Control System Devices Other Than Computers

3.7.3 Default Requirements for Control System Devices

3.8 FIPS 201-2 REQUIREMENT

3.9 DEVICES WITH CONNECTION TO MULTIPLE IP NETWORKS

3.10 SYSTEM AND COMMUNICATION PROTECTION

3.10.1 Denial of Service Protection, Process Isolation and Boundary

Protection

3.10.2 Cryptographic Protection

3.11 SYSTEM AND INTEGRATION INTEGRITY

3.11.1 Malicious Code Protection

3.11.2 Information System Monitoring

3.12 FIELD QUALITY CONTROL

3.12.1 Tests

-- End of Section Table of Contents --

**************************************************************************

USACE / NAVFAC / AFCEC / NASA UFGS-25 05 11 (November 2017)

------------------------------------

Preparing Activity: USACE

UNIFIED FACILITIES GUIDE SPECIFICATIONS

References are in agreement with UMRL dated July 2019

**************************************************************************

SECTION 25 05 11

CYBERSECURITY FOR FACILITY-RELATED CONTROL SYSTEMS

11/17

**************************************************************************

NOTE: This guide specification covers the

requirements for cybersecurity for facility-related

control systems.

Adhere to UFC 1-300-02 Unified Facilities Guide

Specifications (UFGS) Format Standard when editing

this guide specification or preparing new project

specification sections. Edit this guide

specification for project specific requirements by

adding, deleting, or revising text. For bracketed

items, choose applicable item(s) or insert

appropriate information.

Remove information and requirements not required in

respective project, whether or not brackets are

present.

Comments, suggestions and recommended changes for

this guide specification are welcome and should be

as a Criteria Change Request (CCR).

**************************************************************************

**************************************************************************

Note: Facility-related control systems are a subset

of control systems that are used to monitor and

control equipment and systems related to DoD real

property facilities (e.g., building control systems,

utility control systems, electronic security

systems, and fire and life safety systems). This

section includes Cybersecurity requirements to be

included on every DOD project which includes a

facility-related control system. This Section does

not provide general requirements for a control

system, nor are the requirements in this section

sufficient to procure a control system. This

section must be used in conjunction with another

controls system specification. For example, for a

HVAC controls project, this section should be used

in conjunction with Section 23 09 00 and related

sections.

SECTION 25 05 11 Page 4

Requirements and activities in this section must be

coordinated with the other relevant control

specification sections.

This section includes requirements in support of the

DOD Risk Management Framework (RMF) for implementing

cybersecurity. Refer to UFC 4-010-06, Cybersecurity

for Facility-Related Control Systems for

requirements on incorporating cybersecurity into

control system design and for general information on

the RMF process as it applies to control systems.

Assistance for control system cybersecurity is

available from the following Service organizations:

Army: Control System Cybersecurity Center of

Expertise,

Huntsville Engineering and Support Center

Navy: Naval Facilities Engineering Command,

Command Information Office (CIO)

Air Force: Civil Engineer Maintenance,

Inspection, and Repair Team (CEMIRT)

ICS Branch, Tyndall AFB

Marine Corps: Contact Navy POC for Marine Corps

POC information

Since this Section covers a wide range of control

systems, and those systems often have different

capabilities and requirements, there are

requirements identified in this Section which need

extensive designer input or decisions.

Many designer selections in this Section will

require coordination with the project site, System

Owner, Authorizing Official or a subject matter

expert in the specific control systems being

installed.

**************************************************************************

**************************************************************************

NOTE: This Section is for use on control systems

with no impact rating higher than LOW. If the

project includes systems where there systems with

impact ratings of MODERATE or HIGH, this

specification must be modified to include those

additional requirements.

Systems of different types at the same impact level

may have different requirements based on the

specific needs and capabilities of the control

system. This is addressed in this Guide

Specification by indicating when requirements apply

to a specific system type.

Systems of the same type may have different

requirements. This may be due to those systems

having different impact levels or due to

system-specific requirements for systems at the same

SECTION 25 05 11 Page 5

impact level.

If a project includes multiple systems, it's

critical that it be clear which requirements apply

to which systems. This can be done by a) using a

single Section and specifying the applicability of

requirements or b) using multiple Sections. Which

approach to employ depends on the needs of the

project and the preferences of the specifier and

project manager. If using multiple sections use the

fourth level specification numbering to

differentiate the Sections and indicate in each

which systems the Section applies to.

**************************************************************************

**************************************************************************

NOTE: This specification makes use of SpecsIntact

Tailoring Options.

Services tailoring options:

Army

Air Force

Control system type tailoring options:

HVAC Control Systems

Electronic Security Systems (ESS)

**************************************************************************

PART 1 GENERAL

**************************************************************************

NOTE: This subpart points the contractor to the

locations of STIGs and SRGs, as this Section

requires the contractor to meet available STIGs or

SRGs. It's not necessary for the designer/specifier

to review the STIGs or SRGs for applicability. The

contractor is responsible for determining which

STIGs or SRGs are applicable and for meeting the

relevant requirements.

**************************************************************************

Many subparts in this Section contain text in curly braces ("{" and "}")

indicating which cybersecurity control and control correlation identifier

(CCI) the requirements of the subpart relate to. The text inside these

curly braces is for Government reference only, and enables coordination of

the requirements of this Section with the RMF process throughout the

design and construction process. Text in curly braces are not contractor

requirements.

This Section refers to Security Requirements Guide (SRGs) and Security

Technical Implementation Guide (STIGs). STIGs and SRGs are are available

online at the Information Assurance Support Environment (IASE) website at

http://iase.disa.mil/stigs/Pages/index.aspx. Not all control system

components have applicable STIGs or SRGs.

SECTION 25 05 11 Page 6

[1.1 CONTROL SYSTEM APPLICABILITY

**************************************************************************

NOTE: If multiple versions of this Section are used

on a single project, keep this subpart and list all

the systems to which this specific version of the

Section applies.

**************************************************************************

There are multiple versions of this Section associated with this project.

Different versions have requirements applicable to different control

systems. This specific Section applies only to the following control

systems: [_____].

]1.2 RELATED REQUIREMENTS

All Sections containing facility-related control systems or control system

components are related to the requirements of this Section. Review all

specification sections to determine related requirements.

1.3 REFERENCES

**************************************************************************

NOTE: This paragraph is used to list the

publications cited in the text of the guide

specification. The publications are referred to in

the text by basic designation only and listed in

this paragraph by organization, designation, date,

and title.

Use the Reference Wizard's Check Reference feature

when you add a RID outside of the Section's

Reference Article to automatically place the

reference in the Reference Article. Also use the

Reference Wizard's Check Reference feature to update

the issue dates.

References not used in the text will automatically

be deleted from this section of the project

specification when you choose to reconcile

references in the publish print process.

**************************************************************************

The publications listed below form a part of this specification to the

extent referenced. The publications are referred to within the text by

the basic designation only.

AMERICAN SOCIETY OF HEATING, REFRIGERATING AND AIR-CONDITIONING

ENGINEERS (ASHRAE)

ASHRAE 135 (2016) BACnet—A Data Communication

Protocol for Building Automation and

Control Networks

INSTITUTE OF ELECTRICAL AND ELECTRONICS ENGINEERS (IEEE)

IEEE 802.1x (2010) Local and Metropolitan Area

SECTION 25 05 11 Page 7

Networks - Port Based Network Access

Control

NATIONAL INSTITUTE OF STANDARDS AND TECHNOLOGY (NIST)

NIST FIPS 201-2 (2013) Personal Identity Verification

(PIV) of Federal Employees and Contractors

U.S. DEPARTMENT OF DEFENSE (DOD)

DODI 8551.01 (2014) Ports, Protocols, and Services

Management (PPSM)

DTM 08-060 (2008) Policy on Use of Department of

Defense (DoD) Information Systems -

Standard Consent Banner and User Agreement

1.4 DEFINITIONS

1.4.1 Computer

As used in this Section, a computer is one of the following:

a. a device running a non-embedded desktop or server version of Microsoft

Windows

b. a device running a non-embedded version of MacOS

c. a device running a non-embedded version of Linux

d. a device running a version or derivative of the Android OS, where

Android is considered separate from Linux

e. a device running a version of Apple iOS

1.4.2 Network Connected

A component is network connected (or "connected to a network") only when

the device has a network transceiver which is directly connected to the

network and implements the network protocol. A device lacking a network

transceiver (and accompanying protocol implementation) can never be

considered network connected. Note that a device connected to a non-IP

network is still considered network connected (an IP connection or IP

address is not required for a device to be network connected).

Any device that supports wireless communication is network connected,

regardless of whether the device is communicating using wireless.

1.4.3 User Account Support Levels

The support for user accounts is categorized in this Section as one of

three levels:

1.4.3.1 FULLY Supported

Device supports configurable individual accounts. Accounts can be

created, deleted, modified, etc. Privileges can be assigned to accounts.

SECTION 25 05 11 Page 8

1.4.3.2 MINIMALLY Supported

Device supports a small, fixed number of accounts (perhaps only one).

Accounts cannot be modified. A device with only a "User" and an

"Administrator" account would fit this category. Similarly, a device with

two PINs for logon - one for restricted and one for unrestricted rights

would fit here (in other words, the accounts do not have to be the

traditional "user name and password" structure).

1.4.3.3 NOT Supported

Device does not support any Access Enforcement therefore the whole concept

of "account" is meaningless.

1.4.4 User Interface

Generally, a user interface is hardware on a device allowing user

interaction with that device via input (buttons, switches, sliders,

keyboard, touch screen, etc.) and a screen. There are three types of user

interfaces defined in this Section: Limited Local User Interface, Full

Local User Interface and Remote User Interface. In this Section, when the

term "User Interface" is used without specifying which type, it refers

only to Full Local User Interface and Remote User Interface (NOT to

Limited Local User Interface).

1.4.4.1 Limited Local User Interface

A Limited Local User Interface is a user interface where the interaction

is limited, fixed at the factory, and cannot be modified in the field.

The user must be physically at the device to interact with it.

Examples of Limited Local User Interface include thermostats (Space Sensor

Modules as defined in Section 23 09 13 INSTRUMENTATION AND CONTROL DEVICES

FOR HVAC).

1.4.4.2 Full Local User Interface

A Full Local User Interface is a user interface where the interaction and

displays are field-configurable.

Examples of a Full Local User Interface include local applications on a

computer and user interfaces to Variable Speed Drives.

1.4.4.3 Remote User Interface

A Remote User Interface is a user interface on a Client device allowing

user interaction with a different Server device. The user need not be

physically at the Server device to interact with it.

Examples of Remote User Interfaces include web browsers and Local Display

Panels as defined in Section 23 09 00 INSTRUMENTATION AND CONTROL FOR HVAC.

1.5 ADMINISTRATIVE REQUIREMENTS

1.5.1 Coordination

**************************************************************************

NOTE: This subpart deals with coordination

requirements for the contractor, and does not

SECTION 25 05 11 Page 9

indicate coordination that must be done by the

designer/specifier. In addition to the normal

project coordination, authorization for wireless

use, alternate account lock permissions and devices

with multiple IP connections may be impacted by site

(or Service) policies and need to be coordinated

with the appropriate Government representatives

before authorization is provided.

**************************************************************************

Coordinate the execution of this Section with the execution of all other

Sections related to control systems as indicated in the paragraph RELATED

REQUIREMENTS. Items that must be considered when coordinating project

efforts include but are not limited to:

a. If requesting permission for wireless communication, the Wireless

Communication Request submittal must be approved prior to control

system device selection and integration.

b. If requesting permission for alternate account lock permissions, the

Device Account Lock Exception Request must be approved prior to

control system device selection and integration.

c. If requesting permission for the use of a device with multiple IP

connections, the Multiple IP Connection Device Request must be

approved prior to control system device selection and integration.

d. Wireless testing may be required as part of the control system

testing. See requirements for the Wireless Communication Test Report

submittal.

e. If the Device Audit Record Upload Software is to be installed on a

computer not being provided as part of the control system,

coordination is required to identify the computer on which to install

the software.

f. Cybersecurity Interconnection Schedule must be coordinated with other

work that will be interconnected to, and interconnections must be

approved by the Government before relying on them for system

functionality.

g. Cybersecurity testing support must be coordinated across control

systems and with the Government cybersecurity testing schedule.

h. Passwords must be coordinated with the indicated contact for the

project site.

i. If applicable, HTTP web server certificates must be obtained from the

indicated contact for the project site.

j. Contractor Computer Cybersecurity Compliance Statements for each

contractor using contractor owned computers.

1.6 SUBMITTALS

**************************************************************************

NOTE: Review Submittal Description (SD) definitions

in Section 01 33 00 SUBMITTAL PROCEDURES and edit

the following list to reflect only the submittals

SECTION 25 05 11 Page 10

required for the project.

The Guide Specification technical editors have

designated those items that require Government

approval, due to their complexity or criticality,

with a "G." Generally, other submittal items can be

reviewed by the Contractor's Quality Control

System. Only add a "G" to an item, if the submittal

is sufficiently important or complex in context of

the project.

For submittals requiring Government approval on Army

projects, a code of up to three characters within

the submittal tags may be used following the "G"

designation to indicate the approving authority.

Codes for Army projects using the Resident

Management System (RMS) are: "AE" for

Architect-Engineer; "DO" for District Office

(Engineering Division or other organization in the

District Office); "AO" for Area Office; "RO" for

Resident Office; and "PO" for Project Office. Codes

following the "G" typically are not used for Navy,

Air Force, and NASA projects.

An "S" following a submittal item indicates that the

submittal is required for the Sustainability

eNotebook to fulfill federally mandated sustainable

requirements in accordance with Section 01 33 29

SUSTAINABILITY REPORTING. Locate the "S" submittal

under the SD number that best describes the

submittal item.

Choose the first bracketed item for Navy, Air Force

and NASA projects, or choose the second bracketed

item for Army projects.

**************************************************************************

**************************************************************************

NOTE: All submittals in this Guide Specification

require Government approval and must have a "G"

designation.

Government review of submittals in this Section

impact Cybersecurity, and must be coordinated with

the appropriate Cybersecurity experts to ensure

appropriate review and the identification of issues

or concerns that may affect the cybersecurity

posture of the system or the ability of the system

to receive an RMF authorization.

**************************************************************************

Government approval is required for submittals with a "G" designation;

submittals not having a "G" designation are [for Contractor Quality

Control approval.][for information only. When used, a designation

following the "G" designation identifies the office that will review the

submittal for the Government.] Submittals with an "S" are for inclusion

in the Sustainability eNotebook, in conformance with Section 01 33 29

SUSTAINABILITY REPORTING. Submit the following in accordance with Section

SECTION 25 05 11 Page 11

01 33 00 SUBMITTAL PROCEDURES:

SD-01 Preconstruction Submittals

Wireless Communication Request; G[, [_____]]

Device Account Lock Exception Request; G[, [_____]]

Multiple IP Connection Device Request; G[, [_____]]

Contractor Computer Cybersecurity Compliance Statements; G[,

[_____]]

Contractor Temporary Network Cybersecurity Compliance Statements; G

[, [_____]]

SD-02 Shop Drawings

User Interface Banner Schedule; G[, [_____]]

Network Communication Report; G[, [_____]]

Cybersecurity Riser Diagram; G[, [_____]]

Control System Inventory Report; G[, [_____]]

Cybersecurity Interconnection Schedule; G[, [_____]]

SD-03 Product Data

Control System Cybersecurity Documentation; G[, [_____]]

SD-06 Test Reports

Wireless Communication Test Report; G[, [_____]]

SD-07 Certificates

Software Licenses; G[, [_____]]

SD-11 Closeout Submittals

Password Summary Report; G[, [_____]]

Software Recovery And Reconstitution Images; G[, [_____]]

Device Audit Record Upload Software; G[, [_____]]

1.7 QUALITY CONTROL

[1.7.1 Regulatory Requirements

**************************************************************************

NOTE: If there are regulatory requirements related

to a control system, specify those in the control

system specification. If there are regulatory

requirements related to cybersecurity for a control

system they can be specified here.

Regulatory requirements specified here must indicate

SECTION 25 05 11 Page 12

which system or systems they apply to, DO NOT

include requirements here that are not directly

linked to a specific control system.

For typical UMCS or building control system projects

there will not be requirements to include here.

**************************************************************************

For the [_____] control system: [_____].

][1.7.2 [Certifications][Qualifications]

**************************************************************************

NOTE: If there are contractor qualification or

certification requirements related to the control

system, specify those in the control system

specification. If there are contractor

qualifications or certifications specifically

related to cybersecurity they can be specified here.

Use care when including requirements here, as many

cybersecurity certifications are IT-centric and do

not apply to control systems.

Requirements specified here must indicate which

system or systems they apply to, DO NOT include

requirements here that are not directly linked to a

specific control system.

For typical UMCS or building control system projects

there will not be requirements to include here.

**************************************************************************

For the [_____] control system: [_____].

][1.7.3 Pre-Construction Testing

**************************************************************************

NOTE: If there are cybersecurity Pre-Construction

Testing requirements, include them here.

For a LOW-LOW-LOW Impact system pre-construction

testing will generally not be required. For systems

with a MODERATE or HIGH impact there may be some

pre-construction testing requirements based on the

specific needs of the project site.

Requirements specified here must indicate which

system or systems they apply to, DO NOT include

requirements here that are not directly linked to a

specific control system.

**************************************************************************

For the [_____] control system: [_____].

SECTION 25 05 11 Page 13

][1.8 DELIVERY, STORAGE, AND HANDLING

**************************************************************************

NOTE: If there are delivery, storage or handling

requirements, include them here.

For a LOW-LOW-LOW Impact system delivery, storage

and handling requirements will generally not be

needed. For systems with a MODERATE or HIGH impact

there may be some requirements based on the specific

needs of the project site.

**************************************************************************

[_____]

]1.9 CYBERSECURITY DOCUMENTATION

[1.9.1 Cybersecurity Interconnection Schedule

**************************************************************************

NOTE: The Cybersecurity Interconnection Schedule is

used in two situations:

1) The control system communicates with a separately

authorized system or an unauthorized system. In

this case, include a Cybersecurity Interconnection

Schedule in the design showing the following

interconnection details: Name/description of other

system, POC for the other system, type of

data/information.

2) The control system is a sub-part of a larger

system and will communicate with and integrate to

the larger system (and will be part of the same

authorization as the larger system). In this case,

the control system design must include requirements

for the expected communication between the

sub-system and the larger system. The Cybersecurity

Interconnection Schedule will not be a design

drawing, but will still be a contractor submittal.

If neither of these situations apply (if the system

is stand-alone with no connection or integration to

another system), remove the bracketed text requiring

the Cybersecurity Interconnection Schedule, and

remove the Cybersecurity Interconnection Schedule

from the SUBMITTALS paragraph of this Section.

If Case 1 applies, keep the bracketed text referring

to Foreign Destination and POC for Destination,

otherwise remove this text.

In situations where both cases apply, a single

submittal will serve both purposes.

Note that this submittal does not create a

requirement for interconnections, but documents

interconnection details in accordance with other

SECTION 25 05 11 Page 14

requirements.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to CA-3(b),

CCI-00258}

Provide a completed Cybersecurity Interconnection Schedule documenting

connections between the installed system and other systems. Provide the

following information for each device communicating between systems:

Device Identifier, Device Description, Transport layer Protocol, Network

Address, Port (if applicable), MAC (Layer 2) address (if applicable),

Media, Application Protocol, Service (if applicable), Descriptive Purpose

of communication. [For communication with other authorized systems also

provide the Foreign Destination and POC for Destination.] If other

control system Sections used on this project include submittals

documenting this information, provide copies of those submittals to meet

this requirement.

In addition to the requirements of Section 01 33 00 SUBMITTAL PROCEDURES,

provide the Cybersecurity Interconnection Schedule as an editable

Microsoft Excel file (a template Cybersecurity Interconnection Schedule in

Excel format is available at

http://www.wbdg.org/ffc/dod/unified-facilities-guide-specifications-ufgs/forms-graphics-tables

]1.9.2 Network Communication Report

**************************************************************************

NOTE: Control system specifications should include

requirements related to protocol and documentation.

In the design cybersecurity documentation required

by the UFC, document what, if any, protocol

requirements are included in the control system

specification (CCI-002103). Also document any

requirements or submittals related to network

communication, such as Points Schedules

(CCI-002105).

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to CA-9;

CCI-002102, CCI-002103, CCI-002104, CCI-002105 and also the submittal

requirements associated with CM-6, CM-7 and SC-41}

Provide a network communication report. For each networked controller,

document the communication characteristics of the controller including

communication protocols, services used, and a general description of what

information is communicated over the network. For each controller using

IP, document all TCP and UDP ports used. If other control system Sections

used on this project include submittals documenting this information,

provide copies of those submittals to meet this requirement.

In addition to the requirements of Section 01 33 00 SUBMITTAL PROCEDURES,

provide the Network Communication Report as an editable Microsoft Excel

file.

1.9.3 Control System Inventory Report

**************************************************************************

NOTE: Select whether the inventory report must

SECTION 25 05 11 Page 15

include non-networked devices.

Unless specifically required by the project, keep

the first bracketed text to require inventory of

only networked devices and remove the later

bracketed text requiring inventory of non-networked

devices, input devices and output devices.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to CM-8(a),

CP-12, SI-17, IA-3; CCI-000389, CCI-000392, CCI-000398, CCI-002855,

CCI-002856, CCI-002857, CCI-002773, CCI-002774, CCI-002775, CCI-000777,

CCI-000778, CCI-001958}

Provide a Control System Inventory report using the Inventory Spreadsheet

listed under this Section at

http://www.wbdg.org/ffc/dod/unified-facilities-guide-specifications-ufgs/forms-graphics-tables

documenting all [networked devices, including network infrastructure

devices][devices, including networked devices, network infrastructure

devices, non-networked devices, input devices (e.g. sensors) and output

devices (e.g. actuators)]. For each device provide all applicable

information for which there is a field on the spreadsheet in accordance

with the instructions on the spreadsheet.

In addition to the requirements of Section 01 33 00 SUBMITTAL PROCEDURES,

provide the Control System Inventory Report as an editable Microsoft Excel

file.

1.9.4 Software Recovery and Reconstitution Images

**************************************************************************

NOTE: This requirement covers disk images to allow

recovery and reconstitution of applications on

computers. As described in UFC 4-010-06

Cybersecurity for Facility-Related Control Systems,

as-built documentation (including copies of custom

programming and device settings) must be required in

the Section specifying the control system itself.

This requirement covers computers only. If recovery

images of other control system devices (controllers)

are needed, that should be specified in the relevant

control system Section or added here. Use caution

when adding a requirement for controllers here as

not all systems have the same capabilities and a

general requirement here could result in a

conflicting or impractical requirement.

If the contractor is installing software on a

Government Furnished computer to which they may not

have sufficient permissions, include the bracketed

text and indicate a POC for assistance with creating

the image.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to CP-10;

CCI-000550, CCI-000551, CCI-000552}

SECTION 25 05 11 Page 16

For each computer on which software is installed under this project,

provide a recovery image of the final as-built computer. This image must

allow for bare-metal restore such that restoration of the image is

sufficient to restore system operation to the imaged state without the

need for re-installation of software.[

If additional user permissions are required to meet this requirement,

coordinate the creation of the image with [_____].]

1.9.5 Cybersecurity Riser Diagram

**************************************************************************

NOTE: Select or specify the format for the riser

diagram.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to PL-2(a);

CCI-003051, CCI-003053}

Provide a cybersecurity riser diagram of the complete control system

including all network and controller hardware. If the control system

specifications require a riser diagram submittal, provide a copy of that

submittal as the cybersecurity riser diagram. Otherwise, provide a riser

diagram in [one-line format][one-line format overlayed on a facility

schematic][tabular format][_____].

1.9.6 Control System Cybersecurity Documentation

**************************************************************************

NOTE: The following enumerates very detailed

requirements for documentation; requirements that

would be impossible to meet for some control

devices. The requirements are broken out in the sub

paragraphs:

1) Requirements to be met by all software

running on computers

2) Requirements to be met by HVAC control devices

3) Requirements to be met by [fill in the blank]

control devices

4) Default requirements for control system

devices (when not covered in 1-3 above)

If the project incorporates devices other than HVAC

devices, and the general requirements in

sub-paragraph 4 are not satisfactory, add

requirements to subparagraph 3. If multiple

different requirements are needed (e.g. the project

incorporates a micro-grid and and an electronic

security system, both with specific requirements)

add additional paragraphs similar to paragraph 3.

Leave the "devices not otherwise covered" at the end

of the list and do not edit those requirements.

Note that within HVAC devices, a further distinction

is made between devices that FULLY support accounts

and those that do not. This distinction is a

surrogate to account for the range of capabilities

and complexity among various HVAC control devices.

SECTION 25 05 11 Page 17

**************************************************************************

This subpart (and its subparts) relates to SA-5 (a),(b),(c); CCIs:

CCI-003124, CCI-003125, CCI-003126, CCI-003127, CCI-003128, CCI-003129,

CCI-003130, CCI-003131}

Provide a Control System Cybersecurity Documentation submittal containing

the indicated information for each device and software application.

1.9.6.1 Software Applications

For all software applications running on computers provide:

a. administrator documentation that describes secure configuration of the

software {relates to CCI-003124}

b. administrator documentation that describes secure installation of the

software {relates to CCI-003125}

c. administrator documentation that describes secure operation of the

software {relates to CCI-003124}

d. administrator documentation that describes effective use and

maintenance of security functions or mechanisms for the software

{relates to CCI-003127}

e. administrator documentation that describes known vulnerabilities

regarding configuration and use of administrative (i.e. privileged)

functions for the software {relates to CCI-003128}

f. user documentation that describes user-accessible security functions

or mechanisms in the software and how to effectively use those

security functions or mechanisms {relates to CCI-003129}

g. user documentation that describes methods for user interaction which

enables individuals to use the software in a more secure manner

{relates to CCI-003130}

h. user documentation that describes user responsibilities in maintaining

the security of the software {relates to CCI-003131}

1.9.6.2 For HVAC Control System Devices

1.9.6.2.1 HVAC Control System Devices FULLY Supporting User Accounts

For all HVAC Control System Devices which FULLY support user accounts,

provide:

a. Documentation that describes secure configuration of the device {for

reference only: relates to CCI-003124}

b. Documentation that describes secure operation of the device {for

reference only: relates to CCI-003124}

c. Documentation that describes effective use and maintenance of security

functions or mechanisms for the device {for reference only: relates to

CCI-003127}

SECTION 25 05 11 Page 18

d. Documentation that describes known vulnerabilities regarding

configuration and use of administrative (i.e. privileged) functions

for the device {for reference only: relates to CCI-003128}

e. Documentation that describes user-accessible security functions or

mechanisms in the device and how to effectively use those security

functions or mechanisms; or a specific indication that there are no

user-accessible security functions or mechanisms in the device {for

reference only: relates to CCI-003129}

f. Documentation that describes methods for user interaction which

enables individuals to use the device in a more secure manner {for

reference only: relates to CCI-003130}

1.9.6.2.2 All Other HVAC Control System Devices

For all HVAC Control System Devices which do not FULLY support user

accounts, provide:

a. Documentation that describes secure configuration of the device; or a

specific indication that there are no secure configuration steps that

apply {for reference only: relates to CCI-003124}

b. Documentation that describes effective use and maintenance of security

functions or mechanisms for the device; or a specific indication that

there are no security functions or mechanisms in the device {for

reference only: relates to CCI-003127}

c. For devices which include a user interface, documentation that

describes methods for user interaction which enables individuals to

use the device in a more secure manner {for reference only: relates to

CCI-003130}

[1.9.6.3 [_____] Control System Devices

**************************************************************************

NOTE: Use this bracketed subpart if needed to add

requirements for a specific control system type

(e.g. lighting, electrical distribution etc),

similar to how HVAC control system devices are

covered above.

If adding a new control system type, submit a

Criteria Change Request with the relevant

requirements to have that system included in the

published UFGS.

**************************************************************************

[_____]

]1.9.6.4 Default Requirements for Control System Devices

**************************************************************************

NOTE: Do not edit these requirements. If these

requirements do not apply to a specific control

system used on the project, include requirements for

that control system using the bracketed subpart

provided above.

**************************************************************************

SECTION 25 05 11 Page 19

For control system devices where Control System Cybersecurity

Documentation requirements are not otherwise indicated in this Section,

provide:

a. Documentation that describes secure configuration of the device {for

reference only: relates to CCI-003124}

b. Documentation that describes secure installation of the device {for

reference only: relates to CCI-003125}

c. Documentation that describes secure operation of the device {for

reference only: relates to CCI-003124}

d. Documentation that describes effective use and maintenance of security

functions or mechanisms for the device {for reference only: relates to

CCI-003127}

e. Documentation that describes known vulnerabilities regarding

configuration and use of administrative (i.e. privileged) functions

for the device {for reference only: relates to CCI-003128}

f. Documentation that describes user-accessible security functions or

mechanisms in the device and how to effectively use those security

functions or mechanisms {for reference only: relates to CCI-003129}

g. Documentation that describes methods for user interaction which

enables individuals to use the device in a more secure manner {for

reference only: relates to CCI-003130}

h. Documentation that describes user responsibilities in maintaining the

security of the device {for reference only: relates to CCI-003131}

1.10 SOFTWARE UPDATE LICENSING

**************************************************************************

NOTE: The installation may procure its own software

update licensing or contract and thus needs less

than 5 years. Alternatively the installation may

require longer than five years (although this will

likely increase the costs significantly).

Coordinate with the installation to determine if

they have any specific requirement; if they don't

then keep the 5 year requirement.

Note that this requirement may already exist in the

control system specifications, in which case it can

removed from this Section (or kept in this Section

and removed from the control system specification).

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to SI-2

(a),(c); CCI-001227, CCI-002605}

In addition to all other licensing requirements, all software licensing

must include licensing of the following software updates for a period [of

no less than 5 years][___]:

SECTION 25 05 11 Page 20

a. Security and bug-fix patches issued by the software manufacturer.

b. Security patches to address any vulnerability identified in the

National Vulnerability Database at http://nvd.nist.gov with a Common

Vulnerability Scoring System (CVSS) severity rating of MEDIUM or

higher.

Provide a single Software Licenses submittal with documentation of the

software licenses for all software provided

1.11 CYBERSECURITY DURING CONSTRUCTION

**************************************************************************

NOTE: The requirements in this subpart do not tie

to cybersecurity specific cybersecurity controls or

CCIs as tightly as most other requirements in this

Section. They are included to provide a basic level

of "cyber hygiene" during the construction process,

and the controls that they are related to are still

noted for reference.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to AC-18,

SA-3, CCI-00258}

In addition to the control system cybersecurity requirements indicated in

this section, meet following requirement throughout the construction

process.

1.11.1 Contractor Computer Equipment

Contractor owned computers may be used for construction. When used,

contractor computers must meet the following requirements:

1.11.1.1 Operating System

The operating system must be an operating system currently supported by

the manufacturer of the operating system. The operating system must be

current on security patches and operating system manufacturer required

updates.

1.11.1.2 Anti-Malware Software

The computer must run anti-malware software from a reputable software

manufacturer. Anti-malware software must be a version currently supported

by the software manufacturer, must be current on all patches and updates,

and must use the latest definitions file. All computers used on this

project must be scanned using the installed software at least once per day.

1.11.1.3 Passwords and Passphrases

The passwords and passphrases for all computers must be changed from their

default values. Passwords must be a minimum of eight characters with a

minimum of one uppercase letter, one lowercase letter, one number and one

special character.

SECTION 25 05 11 Page 21

1.11.1.4 Contractor Computer Cybersecurity Compliance Statements

Provide a single submittal containing completed Contractor Computer

Cybersecurity Compliance Statements for each company using contractor

owned computers. Contractor Computer Cybersecurity Compliance Statements

must use the template published at

http://www.wbdg.org/ffc/dod/unified-facilities-guide-specifications-ufgs/forms-graphics-tables

Each Statement must be signed by a cybersecurity representative for the

relevant company.

1.11.3 Government Access to Network

Government personnel must be allowed to have complete and immediate access

to the network at any time in order to verify compliance with this

specification

1.11.5 Passwords and Passphrases

The passwords and passphrases for all network devices and network access

must be changed from their default values. Passwords must be a minimum 8

characters with a minimum of one uppercase letter, one lowercase letter,

one number and one special character.

1.11.6 Contractor Temporary Network Cybersecurity Compliance Statements

Provide a single submittal containing completed Contractor Temporary

Network Cybersecurity Compliance Statements for each company implementing

a temporary IP network. Contractor Temporary Network Cybersecurity

Compliance Statements must use the template published at

SECTION 25 05 11 Page 22

http://www.wbdg.org/ffc/dod/unified-facilities-guide-specifications-ufgs/forms-graphics-tables

Each Statement must be signed by a cybersecurity representative for the

relevant company. If no temporary IP networks will be used, provide a

single copy of the Statement indicating this.

1.12 CYBERSECURITY DURING WARRANTY PERIOD

All work performed on the control system after acceptance must be

performed using Government Furnished Equipment or equipment specifically

and individually approved by the Government.

PART 2 PRODUCTS

(NOT USED)

PART 3 EXECUTION

3.1 ACCESS CONTROL REQUIREMENTS

3.1.1 User Accounts

**************************************************************************

NOTE: Ensure that control system specifications

define roles (such as operator with view-only,

operator with control, control system admin) for

applications which FULLY support accounts.

Different devices, particularly those with very

different functions and residing at different places

in the system architecture, may require different

account roles.

DO NOT ALLOW AN INTERFACE THAT DOES NOT SUPPORT

ACCOUNTS TO HAVE THE CAPABILITY TO ALTER THE CONTROL

SYSTEM.

The determination of whether a device has a STIG or

SRG, and the installation and configuration of

devices in accordance with relevant STIGs or SRGs

are contractor responsibilities. The

designer/specifier is not expected to identify

relevant STIGs or SRGs

**************************************************************************

{For Reference Only: This subpart (and its subparts) relate to AC-2(a)and

AC-3; CCI-002110, CCI-000213.}

Any device supporting user accounts (either FULLY or MINIMALLY) must limit

access to the device according to specified limitations for each account.

Install and configure any device having a STIG or SRG in accordance with

that STIG or SRG.

User access hierarchy to EBCS will be structured within these five primary categories:

- Enterprise Admin: full read, write, and invoke privileges at the highest level

- Enterprise User: read-only privileges at the highest level

- Regional Admin: full read, write, and invoke privileges limited within the region as specified by the project POC

- Regional Operator: read-only privileges limited within the region as specified by the project POC

- Local Access: full read, write, and invoke privileges at a single location only as specified by the project POC. Intend for support contractors and temporary access.

3.1.1.1 Computers

All computers must FULLY support user accounts.

3.1.1.2 For HVAC Control System Devices

Devices with web interfaces must either FULLY support user accounts or

have their web interface disabled. Field devices with full local user

SECTION 25 05 11 Page 23

interfaces allowing modification of data must at least MINIMALLY support

user accounts.

[3.1.1.3 [_____] Control System Devices

**************************************************************************

NOTE: Use this bracketed subpart if needed to add

requirements for a specific control system type

(e.g. lighting, electrical distribution etc),

similar to how HVAC control system devices are

covered above.

If adding a new control system type, submit a

Criteria Change Request with the relevant

requirements to have that system included in the

published UFGS.

**************************************************************************

[_____]

]3.1.1.4 Default Requirements for Control System Devices

**************************************************************************

NOTE: Do not edit these requirements (beyond

selection of bracketed text). If these requirements

do not apply to a specific control system used on

the project, include requirements for that control

system using the bracketed subpart provided above.

**************************************************************************

**************************************************************************

NOTE: Select the appropriate minimum account support

for web interfaces.

Select the appropriate minimum account support for

local user interfaces allowing modification of

data. In general, keep "at least MINIMALLY" unless

otherwise required for the project.

Keep or include user account requirements for

read-only interfaces. If keeping the requirement,

select the appropriate user account support. In

general either remove this text (to allow read-only

interfaces with no accounts) or keep "at least

MINIMALLY" unless otherwise required for the project.

Unless specifically required by the project DO NOT

keep bracketed text requiring all devices to at

least MINIMALLY support accounts as this increases

system complexity and cost and requires operation

and maintenance staff to maintain passwords for all

devices.

**************************************************************************

For control system devices where User Account requirements are not

otherwise indicated in this Section:

a. Devices with web interfaces must either [FULLY][at least MINIMALLY]

SECTION 25 05 11 Page 24

support user accounts or have their web interface disabled.

b. Field devices with full local user interfaces allowing modification of

data must [at least MINIMALLY][FULLY] support user accounts.

[ c. Field devices with read-only full local user interfaces must [at least

MINIMALLY][FULLY] support user accounts.

][d. All devices must at least MINIMALLY support user accounts.

]3.1.2 Unsuccessful Logon Attempts

**************************************************************************

NOTE: Note that most field devices that only

MINIMALLY support accounts (e.g. a Local Display

Panel) cannot be locked. Keep the bracketed text

requiring that these devices lock ONLY if this is a

specific project requirement. If keeping this text,

include requirements on when the interface must lock

and how to unlock. Some unlocking conditions to

consider are: network command or a physical button

which is protected by a locked enclosure.

Note that a requirement for a HIGH availability at

the front end may preclude locking out an account

for failed logon attempts. If the system includes

high availability user interfaces which should not

be locked, include the bracketed text exempting high

availability interfaces and keep the bracketed

table. Indicate in the table the exempt interfaces,

their location and action to take for each in lieu

of locking the screen.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relate AC-7 (a),

AC-7 (b); CCI-000043, CCI-000044, CCI-001423, CCI-002236, CCI-002237,

CCI-002238}

Except for high availability user interfaces indicated as exempt, devices

must meet the indicated requirements for handling unsuccessful logon

attempts.

3.1.2.1 Devices MINIMALLY Supporting Accounts

**************************************************************************

NOTE: Indicate whether devices minimally supporting

accounts must lock based on unsuccessful logon

attempts.

Generally, for LOW Impact control systems, locking

is not required - keep the first bracketed text to

indicate so.

Use care when requiring that devices minimally

supporting account lock to specify a reasonable

requirement that will not introduce an additional

O&M burden.

SECTION 25 05 11 Page 25

**************************************************************************

Devices which MINIMALLY support accounts [are not required to lock based

on unsuccessful logon attempts][must lock the user input when [_____] and

must support unlocking of the user input when [_____]].

3.1.2.2 Devices FULLY Supporting Accounts

**************************************************************************

NOTE: Select or indicate the number and time period

for unsuccessful logon attempts to lock an account.

**************************************************************************

Devices which FULLY support accounts must meet the following

requirements. If a device cannot meet these requirements, document device

capabilities to protect from subsequent unsuccessful logon attempts and

propose alternate protections in a Device Account Lock Exception Request

submittal. Do not implement alternate protection measures without explicit

permission from the Government.

a. It must lock the user account when [three][_____] unsuccessful logon

attempts occur within a [15 minute][_____] interval.

b. Once an account is locked, the account must stay locked until unlocked

by an administrator.

c. Once the indicated number of unsuccessful logon attempts occurs, delay

further logon prompts by 5 seconds.

3.1.2.3 High Availability Interfaces Exempt from Unsuccessful Logon

Attempts Requirements

**************************************************************************

NOTE: Indicate whether or not there are high

availability interfaces which are exempt from

unsuccessful logon attempts requirements. If there

are, specify them in the table provided.

**************************************************************************

[There are no high availability interfaces which are exempt from

unsuccessful logon attempts requirements.][The following high availability

interfaces are exempt from unsuccessful logon attempts requirements:

High Availability Interfaces Exempt from Unsuccessful Logon Attempts Requirements

User Interface Location Action to take in lieu of locking screen

[_____] [_____] [_____]

[_____] [_____] [_____]

[_____] [_____] [_____]

]

3.1.3 System Use Notification

**************************************************************************

NOTE: Note that the point of restricting the

requirement to devices "connected to the network" is

to exclude things like a thermostat that has a PIN

SECTION 25 05 11 Page 26

to lockout changes but isn't networked.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to AC-8;

CCI-000048, CCI-002247, CCI-002243, CCI-002244, CCI-002245, CCI-002246,

CCI-000050, CCI-002248}

Web interfaces must display a warning banner meeting the requirements of

DTM 08-060.

Devices which are connected to a network and have a user interface must

display a warning banner meeting the requirements of DTM 08-060 if capable

of doing so. Devices which are connected to a network and have a user

interface but are not capable of displaying a banner must have a

permanently affixed label displaying an approved banner from DTM 08-060.Labels

must be machine printed or engraved, plastic or metal, designed for

permanent installation, must use a font no smaller than 14 point, and must

provide a high contract between font and background colors.

3.1.3.1 User Interface Banner Schedule

Provide a User Interface Schedule using the format indicated showing each

user interface provided and how the information banner requirement has

been implemented for each user interface.

User Interface Schedule Format

(with sample entries)

User Interface

Description

User Interface

Location

Type of User

Interface

Banner Implementation

Sample 1 Room 1 Remote DTM 08-060 Banner "A" Displayed at

Logon

Sample 2 Room 2 Limited Local DTM 08-060 Banner "B" on Affixed

Label

Sample 3 Room 3 Full Local DTM 08-060 Banner "B" Displayed on

Screen

3.1.4 Permitted Actions Without Identification or Authentication

**************************************************************************

NOTE: These requirements are specifically about

user actions, not actions taken automatically by

control system components.

Notes concerning how this requirement addresses

cybersecurity:

1) This requirement indicates that there are

no actions that can be taken without

identification and authentication for any

user interface where account

support is required.

2) This requirement does not limit actions taken

by a user on a user interface that does not

SECTION 25 05 11 Page 27

support accounts, but other requirements limit

this to READ-ONLY interfaces.

3) Thus the "permitted actions" referred to by

control AC-14 are "viewing read-only

information from devices which are not

required to have user accounts."

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to AC-14;

CCI-000061, CCI-000232}

The control system must require identification and authentication before

allowing any actions by a user acting from a user interface which

MINIMALLY or FULLY supports accounts.

3.1.5 Wireless Access

**************************************************************************

NOTE: Avoid wireless to the greatest extent

possible. Wireless may be considered for retrofits

where running wires would be prohibitive, but other

technologies (such as powerline carrier) should be

considered first.

In general, contractors should never install a

wireless network which carries the IP protocol. The

Air Force may allow wireless IP networks to be

installed in some instances, when it is installed in

accordance with existing site requirements -

coordinate with the project site to determine if

this is required and remove the bracketed text if

not required.

Note that contractors may (where permitted and

supported) USE a government provided wireless IP

network.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to AC-18;

CCI-001438, CCI-001439, CCI-002323, CCI-001441}

Unless explicitly authorized by the Government, do not use any wireless

communication. Any device with wireless communication capability is

considered to be using wireless communication, regardless of whether or

not the device is actively communicating wirelessly, except when wireless

communication has been physically permanently disabled (such as through

the removal of the wireless transceiver).

3.1.5.1 Wireless IP Communications

[Unless specifically approved and installed in accordance with the project

site requirements, d][D]o not install wireless IP networks, including: do

not install a wireless access point; do not install or configure an ad-hoc

wireless network; do not install or configure a WiFi Direct communication.

When explicitly authorized by the Government, wireless IP communication

may be used to communicate with an existing wireless network.

SECTION 25 05 11 Page 28

3.1.5.2 Non-IP Wireless Communication

When non-IP wireless communication is explicitly authorized by the

Government, use the maximum level of encryption supported by the specific

protocol employed and select signal strength and radiated power to the

minimum necessary for reliable communication.

3.1.5.3 Wireless Communication Request

**************************************************************************

NOTE: The wireless communication request submittal

will be used to authorize specific use of wireless

communication, and to indicate whether or not

testing of the signal strength is required. In

general, testing is not required for a LOW impact

system.

There may be project site or Service policies that

govern the use of wireless. Before authorizing

wireless use coordinate with the relevant Service

and project site representatives.

**************************************************************************

Provide a report documenting the proposed use of wireless communication

prior to beginning construction using the Wireless Communication Request

Schedule at

http://www.wbdg.org/ffc/dod/unified-facilities-guide-specifications-ufgs/forms-graphics-tables

For each device proposed to use wireless communication show: the device

identifier, a description of the device, the location of the device, the

device identifiers of other devices communicating with the device, the

protocol used for communication, encryption type and strength, RF

Frequency, Radiated Power in dBm (decibel with a milliwatt reference),

free-space range, and the expected as-installed range.

3.1.5.4 Wireless Communication Testing

**************************************************************************

NOTE: Select or enter appropriate name for the

system-level test of the control system.

Select or indicate the wireless network test

boundary.

**************************************************************************

As part of [Performance Verification Testing (PVT)][Functional Performance

Testing {FPT}][___], conduct testing of wireless communication for all

devices indicated on the approved Wireless Communication Request as

requiring testing.

To test wireless communication, test for wireless network reception at

multiple points along the wireless test boundary in the vicinity of the

wireless device, and record whether a network connection can be

established at each point. The wireless test boundary is [the building

exterior walls][the facility fence line][_____]. If wireless testing is

required, provide a Wireless Communication Test Report documenting the

testing points and results at each point for each wireless device.

SECTION 25 05 11 Page 29

3.2 CYBERSECURITY AUDITING

**************************************************************************

NOTE: Auditing within the control system is a

complex requirement. For standard information

systems, DoD has extensive auditing requirements,

which largely cannot be met within a typical control

system. For more information on auditing, see UFC

4-010-06, Cybersecurity for Facility-Related Control

Systems

DoD requires (see AU-2) the capability to audit the

following events :

a. Successful and unsuccessful attempts to

access, modify, or delete privileges, security

objects, security levels, or categories of

information (e.g. Classification levels)

- generally only applicable to computers.

b. Successful and unsuccessful logon attempts

- generally only applicable to computers and

devices FULLY supporting accounts.

c. Privileged activities or other system level

access - generally only applicable to

computers.

d. Starting and ending time for user access to

the system  - generally only applicable to

computers and devices FULLY supporting

accounts.

e. Concurrent logons from different workstations

- generally only applicable to computers and

devices with web interfaces.

f. Successful and unsuccessful accesses to

objects - generally only applicable to

computers.

g. All program initiations - generally only

applicable to computers; for a controller,

this is covered under kernel module actions,

below.

h. All direct access to the information system

- generally only for computers.

i. All account creations, modifications,

disabling, and terminations - generally only

applicable to devices that FULLY support

accounts.

j. All kernel module load, unload, and restart

- this could apply to computers or devices.

DoD also requires that the selection of which events

get audited is under the control of the Information

SECTION 25 05 11 Page 30

System Security Manager (ISSM).

DoD requires (see AU-3) that audit records contain

the following:

type of event

time of the event

location of the event

source of the event

result of the event

the identity of any individuals or subjects

associated with the event.

Note that much of this information will be not

applicable for field control system devices.

DoD requires that all devices in the system be

capable of auditing events, but allows the ISSM to

select which devices must perform auditing (see

AU-12 (b)).

Note that there is a large gap between what is

theoretically required in terms of a capability

("audit all events at all devices") vs. what is

practical and reasonable to implement in a specific

control system. The designer needs to provide input

on what can and cannot be done in terms of what

devices in the system can perform auditing, and what

events can they audit.

Require implementation for what is possible but do

not require unreasonable requirements. Be prepared

to document/explain impractical requirements if

required by the System Owner (SO) or Authorizing

Official (AO)

Control System Alarms:

Control system alarms should have similar

requirements. The designer should specify what

alarms should be generated, which devices should

perform alarm generation, the accuracy of alarm

timestamps, response to alarm generation failures

(e.g. loss of communication with a field device),

and sufficient storage capacity at the front end to

maintain alarm/event logs for a specified period of

time. These requirements should be defined in the

relevant control system specifications, not in this

Section.

**************************************************************************

3.2.1 Audit Events, Content of Audit Records, and Audit Generation

{For Reference Only: This subpart (and its subparts) relates to

AU-2(a),(c),(d), AU-3, AU-12; CCI-000123, CCI-001571, CCI-000125,

CCI-001485, CCI-000130, CCI-000131, CCI-000132, CCI-00133, CCI-000134,

CCI-001487, CCI-000169, CCI-001459, CCI-000171, CCI-000172, CCI-001910}

For devices that have STIG/SRGs related to audit events, content of audit

records or audit generation, comply with the requirements of those

STIG/SRGs.

SECTION 25 05 11 Page 31

3.2.1.1 Computers

For each computer, provide the capability to select audited events and the

content of audit logs. Configure computers to audit the indicated events,

and to record the indicated information for each auditable event

3.2.1.1.1 Audited Events

Configure each computer to audit the following events:

a. Successful and unsuccessful attempts to access, modify, or delete

privileges, security objects, security levels, or categories of

information (e.g. classification levels)

a. Successful and unsuccessful logon attempts

b. Privileged activities or other system level access

c. Starting and ending time for user access to the system

d. Concurrent logons from different workstations

e. Successful and unsuccessful accesses to objects

f. All program initiations

g. All direct access to the information system

h. All account creations, modifications, disabling, and terminations

i. All kernel module load, unload, and restart

3.2.1.1.2 Audit Event Information To Record

Configure each computer to record, for each auditable event, the following

information (where applicable to the event):

a. What type of event occurred

b. When the event occurred

c. Where the event occurred

d. The source of the event

e. The outcome of the event

f. The identity of any individuals or subjects associated with the event

3.2.1.2 For HVAC Control System Devices

3.2.1.2.1 HVAC Control System Devices FULLY Supporting User Accounts

For devices FULLY supporting accounts, provide the capability to select

audited events, and the contents of audit logs. Configure devices to

audit the following events:

a. Successful and unsuccessful logon attempts to the device

SECTION 25 05 11 Page 32

b. Starting and ending time for user access to the device

c. All account creations, modifications, disabling, and terminations

d. All device shutdown and startup

Configure the device to record for each event the following information

(as applicable): the type of event, when the event occurred and the

identity of any individuals or subjects associated with the event

3.2.1.2.2 Other HVAC Control System Devices

There are no requirements to perform auditing at HVAC field devices that

do not FULLY support accounts.

[3.2.1.3 [_____] Control System Devices

**************************************************************************

NOTE: Use this bracketed subpart if needed to add

requirements for a specific control system type

(e.g. lighting, electrical distribution etc),

similar to how HVAC control system devices are

covered above.

If adding a new control system type, submit a

Criteria Change Request with the relevant

requirements to have that system included in the

published UFGS.

**************************************************************************

[_____]

]3.2.1.4 Default Requirements for Control System Devices

**************************************************************************

NOTE: Do not edit these requirements (beyond

selection of bracketed text). If these requirements

do not apply to a specific control system used on

the project, include requirements for that control

system using the bracketed subpart provided above.

**************************************************************************

For control system devices where Audit Events, Content of Audit Records,

and Audit Generation are not otherwise indicated in this Section:

3.2.1.4.1 Devices Which FULLY Support Accounts

For each device which FULLY supports accounts, provide the capability to

select audited events and the content of audit logs. Configure devices to

audit the indicated events, and to record the indicated information for

each auditable event

3.2.1.4.1.1 Audited Events

Configure each device to audit the following events:

a. Successful and unsuccessful attempts to access, modify, or delete

privileges, security objects, security levels, or categories of

information (e.g. classification levels)

SECTION 25 05 11 Page 33

a. Successful and unsuccessful logon attempts

b. Privileged activities or other system level access

c. Starting and ending time for user access to the system

d. Concurrent logons from different workstations

e. All account creations, modifications, disabling, and terminations

f. All kernel module load, unload, and restart

3.2.1.4.1.2 Audit Event Information To Record

Configure each computer to record, for each auditable event, the following

information (where applicable to the event):

a. what type of event occurred

b. when the event occurred

c. where the event occurred

d. the source of the event

e. the outcome of the event

f. the identity of any individuals or subjects associated with the event

3.2.1.4.2 Devices Which Do Not FULLY Support Accounts

For each Device which does not FULLY support accounts configure the device

to audit all device shutdown and startup events and to record for each

event the type of event and when the event occurred.

3.2.2 Audit Storage Capacity and Audit Upload

**************************************************************************

NOTE: Select or indicate duration and rate of audit

record generation for field devices. Unless there

is a known need, do not add requirements for

computer storage capability.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to AU-4;

CCI-001848, CCI-001849}

a. For devices that have STIG/SRGs related to audit storage capacity

(CCI-001848 or CCI-001849) comply with the requirements of those

STIG/SRGs.

b. For non-computer control system devices capable of generating audit

records, provide [60][_____] days worth of secure local storage,

assuming [10][_____] auditable events per day.[

c. For computers, provide storage for at least [_____] audit records.]

SECTION 25 05 11 Page 34

3.2.2.1 Device Audit Record Upload Software

**************************************************************************

NOTE: Select or indicate desired export target for

audit upload software.

Select and indicate where upload software is to be

installed, if it is to be installed. If there is no

front end on which to install the software and there

are no computers installed under this project onto

which is should be loaded remove both sets of

bracketed text.

Note that this software may not be required if there

are no devices other than computers which audit

events.

**************************************************************************

For each non-computer device required to audit events, provide, and

license to the Government, software implementing a secure mechanism of

uploading audit records from the device to a computer and of exporting the

uploaded audit records as a [Microsoft Excel file][comma separated value

text file][Microsoft Excel file or comma separated value text

file][_____]. Where different devices use different software, provide

software of each type required to upload audit logs from all devices.

[Install device audit record upload software on the furnished front end

computer in [_____]. ][Install device audit record upload software on

[_____]. ]Submit copies of device audit record upload software. If there

are no non-computer devices requiring auditing, provide a document stating

this in lieu of this submittal.

3.2.3 Response to Audit Processing Failures

**************************************************************************

NOTE: The requirement that audit processing

failures notify a person implies that this control

can only be met at a computer with network access,

not by a control device within the control system.

The action taken should be "overwrite oldest audit

records" if possible; it should almost certainly

never be "shut down information system". Provide a

POC to notify, either the Security Controls Assessor

(SCA) or the Information System Security Officer

(ISSO). Provide a default action.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to AU-5;

CCI-000139, CCI-000140, CCI-001490}.

Front end computers associated with auditing must, in the case of a

failure in the auditing system, notify [_____] via [e-mail][_____]. In

case of an audit failure, if possible, continue to collect audit records

by [overwriting existing audit records][_____].

3.2.4 Time Stamps

{For Reference Only: This subpart (and its subparts) relates to AU-8;

CCI-000159, CCI-001889, CCI-001890}

SECTION 25 05 11 Page 35

3.2.4.1 Computers

**************************************************************************

NOTE: Note that the timing requirement for

computers may require communication through a

firewall to allow NTP or SNTP to get time updates.

**************************************************************************

Computers generating audit records must have internal clocks capable of

providing time with a resolution of 1 second. Clocks must not drift more

than 10 seconds per day.

Configure the system so that each computer generating audit records

maintains accurate time to within 1 second.

3.2.4.2 For HVAC Control System Devices

**************************************************************************

NOTE: For HVAC Control Systems, the timing

requirements inherent in the control systems and

specified in Section 23 09 23.01 LONWORKS DIRECT

DIGITAL CONTROL FOR HVAC AND OTHER BUILDING CONTROL

SYSTEMS, Section 23 09 23.02 BACNET DIRECT DIGITAL

CONTROL FOR HVAC AND OTHER BUILDING CONTROL SYSTEMS,

and Section 25 10 10 UTILITY MONITORING AND CONTROL

SYSTEM (UMCS) FRONT END AND INTEGRATION should be

sufficient.

Unless otherwise required, keep the first bracketed

text ("Time stamp requirements for HVAC Control

Systems are as indicated in the HVAC Control System

specifications.") and remove the timing requirements

in the second bracketed text.

Note that HVAC control devices may not be able to

meet the timing requirements in the second set of

bracketed text.

**************************************************************************

[Time stamp requirements for HVAC Control Systems are as indicated in the

HVAC Control System specifications.][Devices generating audit records must

have internal clocks capable of providing time with a resolution of 1

second. Clocks cannot drift more than 10 seconds per day. Configure the

system so that each device generating audit records maintains accurate

time to within 1 second.]

[3.2.4.3 [_____] Control System Devices

**************************************************************************

NOTE: Use this bracketed subpart if needed to add

requirements for a specific control system type

(e.g. lighting, electrical distribution etc),

similar to how HVAC control system devices are

covered above.

If adding a new control system type, submit a

Criteria Change Request with the relevant

requirements to have that system included in the

SECTION 25 05 11 Page 36

published UFGS.

**************************************************************************

**************************************************************************

NOTE: Indicate the control system and select or

indicate the timing requirements for that control

system.

**************************************************************************

[_____][Time stamp requirements for [_____] Control Systems are as

indicated in the Control System specifications.][Devices generating audit

records must have internal clocks capable of providing time with a

resolution of 1 second. Clocks cannot drift more than 10 seconds per day.

Configure the system so that each device generating audit records

maintains accurate time to within 1 second.]

]3.2.4.4 Default Requirements for Control System Devices

**************************************************************************

NOTE: Do not edit these requirements (beyond

selection of bracketed text). If these requirements

do not apply to a specific control system used on

the project, include requirements for that control

system using the bracketed subpart provided above.

**************************************************************************

For control system devices where Time Stamps requirements are not

otherwise indicated in this Section: Devices generating audit records

must have internal clocks capable of providing time with a resolution of 1

second. Clocks must not drift more than 10 seconds per day. Configure

the system so that each device generating audit records maintains accurate

time to within 1 second.

3.3 REQUIREMENTS FOR LEAST FUNCTIONALITY

**************************************************************************

NOTE: The control system should be designed to have

the least capability possible while still meeting

the minimum needs of the government. This means

disabling unnecessary functionality. Do not install

unnecessary software. Ensure that unnecessary

accounts, maintenance passwords, etc. are all

changed, disabled, or removed.

For systems other than HVAC control systems:

Consider disallowing unrequested user interfaces and

consider disallowing networked sensors/actuators

where they are not required.

**************************************************************************

{For Reference Only: This subpart (and its subparts), along with the

network communication report submittal specified elsewhere in this

section, relates to CM-6 (a), (c), CM-7, CM-7 (1)(b), SC-41; CCI-000363,

CCI-000364, CCI-000365, CCI-001588, CCI-001755, CCI-000381, CCI-000380,

CCI-00382, CCI-001761, CCI-001762, CCI-002544, CCI-002545, CCI-002546.}

For devices that have a STIG or SRG related to Requirements for Least

Functionality (such as configuration settings and port and device I/O

access for least functionality), install and configure the device in

SECTION 25 05 11 Page 37

accordance with that STIG or SRGs.

For HVAC Control Systems: Do not provide devices with user interfaces

where one was not required. Do not use a networked sensor or actuator

where a non-networked sensor or actuator would suffice.

For Other Control Systems: [Do not provide devices with user interfaces

where one was not required.] [Do not use a networked sensor or actuator

where a non-networked sensor or actuator would suffice.]

3.3.1 Non-IP Control Networks

When control system specifications require particular communication

protocols, use only those communication protocols and only as specified.

Do not implement any other communication protocol, or use any protocol on

ports other than those specified.

When control system specifications do not indicate requirements for

communication protocols, use only those protocols required for operation

of the system as specified.

3.3.2 IP Control Networks

Do not use nonsecure functions, ports, protocols and services as defined

in DODI 8551.01 unless those ports, protocols and services are

specifically required by the control system specifications or otherwise

specifically authorized by the Government. Do not use ports, protocols

and services that are not specified in the control system specifications

or required for operation of the control system.

3.4 SAFE MODE AND FAIL SAFE OPERATION

**************************************************************************

NOTE: The designer should determine, based on the

criticality of the controlled equipment, what

conditions to consider and which actions, if any,

including possible alarm requirements, the control

system should take when these conditions are true.

This should include external conditions (e.g. loss

of off-site utility power), internal conditions

(e.g. network or sensor failure), and operator input

(e.g. manual command to a safe mode of operation).

This should all be specified in the control logic

(e.g. sequence of operations), in particular by

addressing normal/failed positions of output

devices, including default positions upon loss of

network, and in the overall system design. Where

high reliability is required, the analysis should

consider the addition of redundant equipment to the

design. See also guidance on SC-24 (Fail in Known

State), guidance on SI-17 (Fail-Safe Procedures) and

the MINIMUM CYBERSECURITY DESIGN REQUIREMENTS in UFC

4-010-06, Cybersecurity for Facility-Related Control

Systems.

Note that any requirements in the control system

needed to meet CP-12 (Safe Mode) or SI-17 (Fail-Safe

Procedures) should be specified in existing

specifications and design, for example, redundant

SECTION 25 05 11 Page 38

AHUs in the mechanical design and sequences of

operation. Any specific requirements for CP-12 or

SI-17 should be addressed in those sections, not in

this UFGS.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to CP-12,

SI-17; CCI-002855, CCI-002856, CCI-002857, CCI-002773, CCI-002774,

CCI-002775}

For all control system components with an applicable STIG or SRG,

configure the component in accordance with all applicable STIGs and SRGs.

3.5 IDENTIFICATION AND AUTHENTICATION

3.5.1 User Identification and Authentication

{For Reference Only: This subpart (and its subparts) relates to

IA-2,(1),(12); CCI-000764, CCI-000765, CCI-001953, CCI-001954}

a. Devices that FULLY support accounts must uniquely identify and

authenticate organizational users.

b. Devices which allow network access to privileged accounts must

implement multifactor authentication for network access to privileged

accounts.

3.5.1.1 HVAC Control Systems Devices

Identification and Authentication for network access to privileged

accounts must be implemented by either accepting and electronically verify

Personal Identity Verification (PIV) credentials or inheriting

identification and authentication from the operating system.

3.5.1.2 Electronic Security System Devices

**************************************************************************

NOTE: Select whether to require PIV, or allow

alternate mechanisms.

**************************************************************************

Identification and Authentication for network access to privileged

accounts must be implemented by [accepting and electronically verifying

Personal Identity Verification (PIV) credentials][or][inheriting

identification and authentication from the operating system][or][_____].

[3.5.1.3 [_____] Control System Devices

**************************************************************************

NOTE: Use this bracketed subpart if needed to add

requirements for a specific control system type

(e.g. lighting, electrical distribution etc),

similar to how HVAC control system devices are

covered above.

If adding a new control system type, submit a

Criteria Change Request with the relevant

requirements to have that system included in the

published UFGS.

SECTION 25 05 11 Page 39

**************************************************************************

[_____]

]3.5.1.4 Default Requirements for Control System Devices

**************************************************************************

NOTE: Select whether to require PIV, or allow

alternate mechanisms.

Do not edit these requirements (beyond selection of

bracketed text). If these requirements do not apply

to a specific control system used on the project,

include requirements for that control system using

the bracketed subpart provided above.

**************************************************************************

For control system devices where User Identification and Authentication

requirements are not otherwise indicated in this Section, User

Identification and Authentication for network access to privileged

accounts must be implemented by [accepting and electronically verify

Personal Identity Verification (PIV) credentials][or][inheriting

identification and authentication from the operating system][or][_____].

3.5.2 Authenticator Management

{For Reference Only: This subpart (and its subparts) relates to IA-5

(b),(c),(e),(g),(1),(11); CCI-000176, CCI-001544, CCI-001989, CCI-000182,

CCI-001610, CCI-000192, CCI-000193, CCI-000194, CCI-000205, CCI-001619,

CCI-001611, CCI-001612, CCI-001613, CCI-001614, CCI-000195, CCI-001615,

CCI-000196, CCI-000197, CCI-000199, CCI-000198, CCI-001616, CCI-001617,

CCI-000200, CCI-001618, CCI-002041, CCI-002002, CCI-002003}

3.5.2.1 Authentication Type

3.5.2.1.1 For HVAC Control System Devices

**************************************************************************

NOTE: Coordinate with the project site to determine

the appropriate authenticator type for software.

**************************************************************************

Unless otherwise indicated:

a. Software which FULLY supports accounts and which runs on a computer

must use [password-based authentication or hardware token-based

authentication][password-based authentication][hardware token-based

authentication].

b. Other devices which FULLY support accounts must use password-based

authentication.

c. Devices MINIMALLY supporting accounts must use password-based

authentication.

[3.5.2.1.2 [_____] Control System Devices

**************************************************************************

NOTE: Use this bracketed subpart if needed to add

SECTION 25 05 11 Page 40

requirements for a specific control system type

(e.g. lighting, electrical distribution etc),

similar to how HVAC control system devices are

covered above.

If adding a new control system type, submit a

Criteria Change Request with the relevant

requirements to have that system included in the

published UFGS.

**************************************************************************

[_____]

]3.5.2.1.3 Default Requirements for Control System Devices

**************************************************************************

NOTE: Do not edit these requirements (beyond

selection of bracketed text). If these requirements

do not apply to a specific control system used on

the project, include requirements for that control

system using the bracketed subpart provided above.

**************************************************************************

**************************************************************************

NOTE: Indicate required authenticator type. Unless

specifically required by the project, do not require

all devices that FULLY support accounts to use

hardware token-based authentication.

**************************************************************************

For control system devices where Authentication Type requirements are not

otherwise indicated in this Section:

a. Software which FULLY supports accounts and which runs on a computer

must use [password-based authentication or hardware token-based

authentication][password-based authentication][hardware token-based

authentication].

b. Other devices which FULLY support accounts must use [either

password-based authentication or hardware token-based

authentication][password-based authentication][hardware token-based

authentication].

c. Devices MINIMALLY supporting accounts must use [either password-based

authentication or hardware token-based authentication][password-based

authentication][hardware token-based authentication].

3.5.2.2 Password-Based Authentication Requirements

3.5.2.2.1 Passwords for Computers

All computers supporting password-based authentication must enforce the

following requirements:

a. Minimum password length of 12 characters

b. Password must contain at least one uppercase character.

c. Password must contain at least one lowercase character.

SECTION 25 05 11 Page 41

d. Password must contain at least one numeric character.

e. Password must contain at least one special character.

f. Password must have a minimum lifetime of 24 hours.

g. Password must have a maximum lifetime of 60 days. When passwords

expire, prompt users to change passwords. Do no lock accounts due to

expired passwords.

h. Password must differ from previous five passwords, where differ is

defined as changing at least 50 percent of the characters.

i. Passwords must be cryptographically protected during storage and

transmission.

3.5.2.2.2 Passwords for Non-Computer Devices FULLY Supporting Accounts

All non-computer devices FULLY supporting accounts and supporting

password-based authentication must enforce the following requirements:

a. Minimum password length of twelve (12) characters

b. Password must contain at least one uppercase character.

c. Password must contain at least one lowercase character.

d. Password must contain at least one numeric character.

e. Password must contain at least one special character.

f. Password must have a maximum lifetime of sixty (60) days. When

passwords expire, prompt users to change passwords. Do no lock

accounts due to expired passwords.

g. Password must differ from previous five (5) passwords, where differ is

defined as changing at least fifty percent of the characters.

h. Passwords must be cryptographically protected during storage and

transmission.

3.5.2.2.3 Passwords for Web Interfaces

Passwords for connecting to a web interface supporting password-based

authentication must enforce the following requirements:

a. Minimum password length of 12 characters

b. Password must contain at least one uppercase character.

c. Password must contain at least one lowercase character.

d. Password must contain at least one numeric character.

e. Password must contain at least one special character.

f. Password must have a maximum lifetime of 60 days. When passwords

expire, prompt users to change passwords. Do no lock accounts due to

expired passwords.

SECTION 25 05 11 Page 42

g. Password must differ from previous five passwords, where differ is

defined as changing at least 50 percent of the characters.

h. Passwords must be cryptographically protected during storage and

transmission.

3.5.2.2.4 Passwords for Devices Minimally Supporting Accounts

**************************************************************************

NOTE: Indicate minimum password requirements for

devices MINIMALLY supporting accounts. Use as large

a value as practical, but use caution to pick a

number that is supportable by the components.

Never allow a minimum length less than four

characters. For HVAC control systems, simple Local

Display Panels may not support more than four

characters, and keeping four as the minimum is

generally recommended.

**************************************************************************

Devices minimally supporting accounts must support passwords with a

minimum length of [four][_____] characters.

3.5.2.2.5 Password Configuration and Reporting

**************************************************************************

NOTE: Provide a POC for password coordination.

This will generally be a supervisor or other senior

member of the project site maintenance organization.

The Password Summary Report is needed by the project

site DPW. This report is required to be delivered

as hardcopy in a sealed envelope to keep passwords

more confidential.

**************************************************************************

For all devices with a password, change the password from the default

password. Coordinate selection of passwords with [_____]. Do not use the

same password for more than one device unless specifically instructed to

do so. Provide a Password Summary Report documenting the password for

each device and describing the procedure to change the password for each

device.

Do not provide the Password Summary Report in electronic format. Provide

[two][_____] hardcopies of the Password Summary Report, each copy in its

own sealed envelope.

3.5.2.3 Hardware Token-Based Authentication Requirements

Devices supporting hardware token-based authentication must use Personal

Identity Verification (PIV) credentials for the hardware token.

3.5.3 Authenticator Feedback

{For Reference Only: This subpart relates to IA-6; CCI-000206}

Devices must never show authentication information, including passwords,

SECTION 25 05 11 Page 43

on a display. Devices that momentarily display a character as it is

entered, and then obscure the character, are acceptable. For devices that

have STIGs or SRGs related to obscuring of authenticator feedback

(CCI-000206), comply with the requirements of those STIGS/SRGs.

3.5.4 Device Identification and Authentication

**************************************************************************

NOTE: Indicate whether certificates for HTTPS will

be provided by a Government POC, and if so who will

provide them. Coordinate this requirement with the

project site, and with the control system

specification as this may already be specified there.

Wireless IP communication needs to be explicitly

permitted via the wireless communication request

submittal, and requires an existing

Government-provided WiFi network. If a WiFi network

is available for potential contractor use, include

the bracketed text requiring wireless IP

authentication and coordinate with the IT staff to

indicate the authentication mechanism. If no WiFi

network will be available, remove this bracketed

text.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to IA-3;

CCI-000777, CCI-000778, CCI-001958}

All computers must use IEEE 802.1x for authentication to the network. All

web servers running on computers must use HTTPS[ and must implement HTTPS

using web server certificates obtained from [_____]].[ When wireless IP

devices are permitted, they must use [_____] for authentication.]

3.5.4.1 For HVAC Control System Devices

**************************************************************************

NOTE: Indicate whether certificates for HTTPS will

be provided, and if so who will provide them.

Unless otherwise required, if the project allows the

Niagara Framework, require Fox Protocol components

to support 802.1x.

If widely supported, require Ethernet devices to

meet 802.1x. Note many IP-based controller do not

support 802.1x, so only include this requirement if

confident it can be sufficiently supported or if it

is a specific project requirement.

Do not require Network Security with BACnet without

determining both a) that it is a specific project

requirement, and b) that it can be met by multiple

vendors.

**************************************************************************

Devices using Fox Protocol must use HTTPS[ using a web server certificate

obtained from [_____]]. [Devices using Fox Protocol must support

IEEE 802.1x. ][Devices using Ethernet must support IEEE 802.1x.

SECTION 25 05 11 Page 44

][Devices using BACnet must support Network Security as specified in

Clause 24 of ASHRAE 135.]

[3.5.4.2 [_____] Control System Devices

**************************************************************************

NOTE: Use this bracketed subpart if needed to add

requirements for a specific control system type

(e.g. lighting, electrical distribution etc),

similar to how HVAC control system devices are

covered above.

If adding a new control system type, submit a

Criteria Change Request with the relevant

requirements to have that system included in the

published UFGS.

**************************************************************************

[_____]

]3.5.4.3 Default Requirements for Control System Devices

**************************************************************************

NOTE: Do not edit these requirements (beyond

selection of bracketed text). If these requirements

do not apply to a specific control system used on

the project, include requirements for that control

system using the bracketed subpart provided above.

If widely supported, require Ethernet devices to

meet 802.1x. Note many IP-based controller do not

support 802.1x, so only include this requirement if

confident it can be sufficiently supported or if it

is a specific project requirement.

Indicate whether certificates for HTTPS will be

provided, and if so who will provide them.

**************************************************************************

For control system devices where Device Identification and Authentication

requirements are not otherwise indicated in this Section: [Devices using

Ethernet must support IEEE 802.1x. ]Devices using HTTP as a control

protocol must use HTTPS[ using a web server certificate obtained from

[_____]] instead.

3.5.5 Cryptographic Module Authentication

**************************************************************************

NOTE: As of July 2017 there are no known STIGs/SRGs

related to this requirement which apply to HVAC

control systems.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to IA-7;

CCI-000803}

For devices that have STIG/SRGs related to cryptographic module

authentication (CCI-000803), comply with the requirements of those

STIG/SRGs.

SECTION 25 05 11 Page 45

3.6 EMERGENCY POWER

**************************************************************************

NOTE: A long term alternate power supply is almost

never required by the control system itself, this

will usually be required (if at all) by tenant

requirements or by the overall system design and

should seldom be added as an ad-hoc requirement.

Control systems for underlying systems with

alternate power should use that alternate power

source.

A UPS may be desired for specific control system

components where rapid recovery after a power outage

is required, or where the control system itself is

necessary for restoration of power. Again, this

should be driven by mission requirements and control

system specifications should already require

adequate system restoration after loss of power.

If there are specific requirements for either

short-term (UPS) or long-term (generator or

alternate power source), include them as part of the

design and in the relevant specification sections

rather than adding requirements to this section.

Note that use of small local UPSes creates

additional maintenance burdens due to the

requirements for periodic battery replacement and

may ultimately result in a less reliable system.

Brackets are provided here for the EXTREMELY RARE

case in which emergency power requirements must be

specified here. In most cases, keep the bracketed

text indicating emergency power requirements are in

accordance with the control system and equipment

specifications.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to

PE-11,(1); CCI-02955, CCI-000961}

[Emergency power is specified in the control system and equipment

specifications.][_____]

3.7 DURABILITY TO VULNERABILITY SCANNING

**************************************************************************

NOTE: In general, it won't be possible to assume

that devices will respond to a scanning tool. There

might be specific cases where it is desirable for

devices to provide specific responses to specific

tools. If so, add the appropriate requirements to

indicate the scanning tools and response information.

For computers, select whether the computer must

respond in specific ways to scans. If so, keep the

bracketed text and define specific scanning tools

and response. If not, remove the bracketed text.

SECTION 25 05 11 Page 46

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to RA-5

(a),(b),(c),(d); CCI-001054, CCI-001055, CCI-0010156, CCI-001641,

CCI-001643, CCI-001057, CCI-001058, CCI-001059}

All IP devices must be scannable, such that the device can be scanned by

industry standard IP network scanning utilities without harm to the

device, application, or functionality.

[Computers must respond to scans from [_____] by responding with a

[_____]. ]For control system devices other than computers:

3.7.1 HVAC Control System Devices Other Than Computers

HVAC control system devices other than computers are not required to

respond to scans.

[3.7.2 [_____] Control System Devices Other Than Computers

**************************************************************************

NOTE: Use this bracketed subpart if needed to add

requirements for a specific control system type

(e.g. lighting, electrical distribution etc),

similar to how HVAC control system devices are

covered above.

If adding a new control system type, submit a

Criteria Change Request with the relevant

requirements to have that system included in the

published UFGS.

**************************************************************************

**************************************************************************

NOTE: Select whether control system devices must

respond to scans and, if so, indicate the tools and

the response required.

**************************************************************************

[_____] control system devices other than computers [must respond to scans

from [_____] by responding with a [_____]][are not required to respond to

scans].

]3.7.3 Default Requirements for Control System Devices

**************************************************************************

NOTE: Do not edit these requirements (beyond

selection of bracketed text). If these requirements

do not apply to a specific control system used on

the project, include requirements for that control

system using the bracketed subpart provided above.

**************************************************************************

**************************************************************************

NOTE: Select whether control system devices must

respond to scans and, if so, indicate the tools and

the response required.

**************************************************************************

SECTION 25 05 11 Page 47

Non-computer control system devices where Durability to Vulnerability

Scanning requirements are not otherwise indicated in this Section [must

respond to scans from [_____] by responding with a [_____]][are not

required to respond to scans].

3.8 FIPS 201-2 REQUIREMENT

**************************************************************************

NOTE: Select brackets to indicate if any systems

require devices using PIV to be on the FIPS 201-2

approved product list.

Many control systems will not be able to meet a

requirement for devices to be on the FIPS 201-2

approved product lists. Only require this when

necessary.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to SA-4

(10); CCI-003116}

Devices in the following systems which implement PIV must be on the

NIST FIPS 201-2 approved product list: [NONE][electronic security

systems(ESS)][_____].

3.9 DEVICES WITH CONNECTION TO MULTIPLE IP NETWORKS

Except for Ethernet switches, do not use more than one physical connection

to IP networks on the same device unless doing so is both required by the

project specifications and the specific application is approved. If a

device with multiple IP connections is required, provide a Multiple IP

Connection Device Request using the Multiple IP Connection Device Request

Schedule at

http://www.wbdg.org/ffc/dod/unified-facilities-guide-specifications-ufgs/forms-graphics-tables

to request approval for each device.

3.10 SYSTEM AND COMMUNICATION PROTECTION

3.10.1 Denial of Service Protection, Process Isolation and Boundary

Protection

**************************************************************************

NOTE: Implementation of boundary protection is

typically outside the scope of the controls

contractor. The site IT staff should implement

boundary protection via rules (e.g. a firewall)

isolating the control system from the wider

network. This is true even for a control system

which will be later integrated to a larger system;

the field point of connection (FPOC) should be

configured to allow the minimum traffic necessary

for operation. Critical to this is the

Cybersecurity Interconnection Schedule, which

defines what traffic must be allowed through the

boundary for the proper operation of the system.

Note that reducing the dependence on the network

helps mitigate threats caused by a weak boundary

defense.

SECTION 25 05 11 Page 48

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to SC-5,

SC-39, SC-7(a); CCI-001093, CCI-002385, CCI-002386, CCI-002430, CCI-001097}

To the greatest extent practical, implement control logic in non-computer

hardware and without reliance on the network.

[3.10.2 Cryptographic Protection

**************************************************************************

NOTE: With regard to cryptography, there are 3

possibilities to consider:

1. The control system contains no classified

information and no cryptography is required. In

that case, there are no UFGS requirements.

2. The control system contains no classified

information, but the Authorizing Official has

determined that cryptography is required. Select

text requiring cryptography.

3. The control system contains classified

information. First, confirm that the system truly

needs to contain classified information - if this is

only to fulfil some reporting requirement, consider

removing the information from the CS and meeting the

reporting requirement via some other means. If the

requirement for cryptography cannot be eliminated,

select text requiring cryptography.

In generally, the need for cryptography should be

avoided, or at least minimized. (Note that even for

systems where cryptography is required, it may not

be required at every node and interconnection in the

system.)

If cryptography is required, select whether to

require it everywhere, only on the IP network, or

only at specific locations within the system.

**************************************************************************

{For Reference Only: This subpart (and its subparts) relates to SC-13;

CCIs: CCI-002449, CCI-002450}

For devices that have STIG/SRGs related to cryptographic protection

(CCI-002450), comply with the requirements of those STIG/SRGs. Ensure

that [all][IP][_____] network traffic is encrypted using NSA-approved

cryptography; provision of digital signatures and hashing, and

FIPS-validated cryptography.

]3.11 SYSTEM AND INTEGRATION INTEGRITY

3.11.1 Malicious Code Protection

{For Reference Only: This subpart (and its subparts) relates to SI-3(c);

CCI-001241, CCI-002623}

For all computers installed under this project, install and configure

malware protection software in accordance with the relevant STIGs.

SECTION 25 05 11 Page 49

[3.11.2 Information System Monitoring

**************************************************************************

NOTE: Delete this subpart unless specifically

required for the project. If required, indicate

requirements for the monitoring of the control

system.

**************************************************************************

{For Reference Only: This subpart relates to SI-4 (a),(b); CCI-001253,

CCI-002645}

[_____]

]3.12 FIELD QUALITY CONTROL

3.12.1 Tests

**************************************************************************

NOTE: Coordinate with the entity performing

cybersecurity testing to determine support

requirements for cybersecurity testing.

Some possible values to consider:

1) A control system with no IP devices: 1-2

days.

2) A control system with IP devices: 5 days

3) If the system includes a new front-end

(server): +5 additional days

**************************************************************************

In addition to testing and testing support required by other Sections,

provide a minimum of [_____] hours of technical support for cybersecurity

testing of control systems.

-- End of Section --

SECTION 25 05 11 Page 50