**************************************************************************

USACE / NAVFAC / AFCEC / NASA UFGS-25 10 10 (February 2019)

-----------------------------

Preparing Activity: USACE Superseding

UFGS-25 10 10 (November 2015)

UNIFIED FACILITIES GUIDE SPECIFICATIONS

References are in agreement with UMRL dated July 2019

**************************************************************************

SECTION TABLE OF CONTENTS

DIVISION 25 - INTEGRATED AUTOMATION

SECTION 25 10 10

UTILITY MONITORING AND CONTROL SYSTEM (UMCS) FRONT END AND INTEGRATION

02/19

PART 1 GENERAL

1.1 SUMMARY

1.1.1 System Requirements

1.1.1.1 General System Requirements

1.1.1.2 LonWorks Requirements

1.1.1.3 BACnet Requirements

1.1.1.4 Modbus Requirements

1.1.1.5 OPC Requirements

1.1.1.6 Niagara Framework Requirements

1.1.2 General Cybersecurity Requirements

1.1.3 Symbols, Definition and Abbreviations

1.1.4 System Units and Accuracy

1.1.5 Data Packages/Submittals Requirements

1.2 REFERENCES

1.3 DEFINITIONS

1.3.1 Alarm Generation

1.3.2 Alarm Handling

1.3.3 Alarm Routing

1.3.4 Application Generic Controller (AGC)(LonWorks)

1.3.5 Application Specific Controller (ASC)(LonWorks)

1.3.6 BACnet (BACnet)

1.3.7 BACnet Advanced Application Controller (B-AAC)(BACnet)

1.3.8 BACnet Advanced Operator Workstation (B-AWS)(BACnet)

1.3.9 BACnet Application Specific Controller (B-ASC)(BACnet)

1.3.10 BACnet Building Controller (B-BC)(BACnet)

1.3.11 BACnet Internetwork (BACnet)

1.3.12 BACnet Interoperability Building Blocks (BIBBs) (BACnet)

1.3.13 BACnet Operator Display (B-OD)(BACnet)

1.3.14 BACnet Operator Workstation (B-OWS)(BACnet)

1.3.15 BACnet Smart Actuator (B-SA)(BACnet)

1.3.16 BACnet Smart Sensor (B-SS)(BACnet)

1.3.17 BACnet Testing Laboratories (BTL)(BACnet)

1.3.18 BACnet Testing Laboratories (BTL) Listed (BACnet)

1.3.19 Binary

1.3.20 Binding (LonWorks)

SECTION 25 10 10 Page 1

1.3.21 Broadcast

1.3.22 Building Control Network (BCN)

1.3.23 Building Control System (BCS)

1.3.24 Building Point of Connection (BPOC)

1.3.25 Channel (LonWorks)

1.3.26 Commandable (BACnet)

1.3.27 Configuration Property (LonWorks)

1.3.28 Control Logic Diagram

1.3.29 Device Object (BACnet)

1.3.30 Explicit Messaging (LonWorks)

1.3.31 External Interface File (XIF) (LonWorks)

1.3.32 Field Point Of Connection (FPOC)

1.3.33 Field Control Network

1.3.34 Field Control System (FCS)

1.3.35 Fox Protocol (Niagara Framework)

1.3.36 Functional Profile (LonWorks)

1.3.37 Gateway

1.3.38 General Purpose Programmable Controller (GPPC) (LonWorks)

1.3.39 Internetwork (BACnet)

1.3.40 JACE (Niagara Framework)

1.3.41 LonMark Object (LonWorks)

1.3.42 LNS Plug-in (LonWorks)

1.3.43 LonMark (LonWorks)

1.3.44 LonMark International (LonWorks)

1.3.45 LonWorks (LonWorks)

1.3.46 LonWorks Network Services (LNS) (LonWorks)

1.3.47 LonWorks Network Services (LNS) Database (LonWorks)

1.3.48 Modbus

1.3.49 Master-Slave/Token Passing (MS/TP)(BACnet)

1.3.50 Monitoring and Control (M&C) Software

1.3.51 Network (BACnet)

1.3.52 Network Variable (LonWorks)

1.3.53 Network Configuration Tool (LonWorks)

1.3.54 Niagara Framework

1.3.55 Niagara Framework Supervisory Gateway (Niagara Framework)

1.3.56 Node (LonWorks)

1.3.57 Node Address (LonWorks)

1.3.58 Node ID (LonWorks)

1.3.59 Object (BACnet)

1.3.60 Override

1.3.61 Point, Calculated

1.3.62 Point, Network

1.3.63 Polling

1.3.64 Program ID (LonWorks)

1.3.65 Property (BACnet)

1.3.66 Protocol Implementation Conformance Statement (PICS)(BACnet)

1.3.67 Repeater

1.3.68 Router (LonWorks)

1.3.69 Router (BACnet)

1.3.70 Segment

1.3.71 Service (BACnet)

1.3.72 Service Pin (LonWorks)

1.3.73 Standard BACnet Object/Property/Service (BACnet)

1.3.74 Standard Configuration Property Type (SCPT) (LonWorks)

1.3.75 Standard Network Variable Type (SNVT) (LonWorks)

1.3.76 Subnet (LonWorks)

1.3.77 Supervisory Controller

1.3.78 Supervisory Gateway

1.3.79 TP/FT-10 (LonWorks)

SECTION 25 10 10 Page 2

1.3.80 TP/XF-1250 (LonWorks)

1.3.81 UMCS Network

1.3.82 User-defined Configuration Property Type (UCPT) (LonWorks)

1.3.83 User-defined Network Variable Type (UNVT) (LonWorks)

1.3.84 Utility Control System (UCS)

1.4 SUBMITTALS

1.5 PROJECT SEQUENCING

1.5.1 Sequencing for Submittals

1.5.2 Sequencing for Activities

1.5.3 Abbreviations

1.6 QUALITY CONTROL (QC) CHECKLISTS

1.7 OPERATION AND MAINTENANCE (O&M) INSTRUCTIONS

PART 2 PRODUCTS

2.1 EQUIPMENT REQUIREMENTS

2.1.1 Product Certifications

2.1.2 Product Sourcing

2.1.3 General Requirements

2.1.4 Nameplates

2.1.5 Product Data Sheets

2.2 CONTROL HARDWARE

2.2.1 Control Protocol Routers

2.2.1.1 LonWorks/IP Router

2.2.1.2 BACnet/IP Router

2.2.1.3 Modbus/IP Router

2.2.2 Monitoring and Control (M&C) Controller Hardware

2.2.3 BACnet Supervisory Controller Hardware

2.2.4 Control Protocol Gateways

2.2.4.1 Gateway for CEA-709.1

2.2.4.2 Gateway for ASHRAE 135

2.2.4.3 Gateway for Modbus

2.2.4.4 Gateway for OPC

2.2.4.5 Gateway for DNP3

2.2.4.6 Niagara Framework Supervisory Gateway

2.4.6 CEA-852-C Configuration Server

2.4.7 CEA-709.1-D Network Configuration Tool

2.4.8 BACnet Network Browser

2.4.9 Niagara Framework Engineering Tool

2.4.10 Monitoring and Control (M&C) Software

2.4.10.1 M&C Software License

2.4.10.1.1 Network Points

2.4.10.1.2 Web Clients

2.4.10.1.3 Calculations

2.4.10.1.4 Other Points

2.4.10.1.5 Alarming

2.4.10.1.6 Trending

2.4.10.1.7 Scheduling

2.4.10.1.8 Niagara Framework Open License

2.4.10.2 M&C Software Update Licensing

2.4.10.3 Supported Field Control Protocols

2.4.10.4 Supported Enterprise Protocols

2.4.10.5 Point Information

2.4.10.5.1 Name

2.4.10.5.2 Description

2.4.10.5.3 Value

2.4.10.5.4 Units

2.4.10.5.5 Source

2.4.10.6 Point Calculations

2.4.10.7 Browser-Based Graphical User Interface (GUI)

2.4.10.8 Passwords

2.4.10.9 Graphical System Displays

2.4.10.9.1 Navigation Scheme

2.4.10.9.2 Navigation Commands

2.4.10.10 Graphic Editor

2.4.10.11 System Display Editor

2.4.10.12 Scheduling

SECTION 25 10 10 Page 4

2.4.10.13 Alarms

2.4.10.14 Trending

2.4.10.15 Electrical Power Demand Limiting

2.4.10.16 Report Generation

2.4.10.17 Custom Report Generation

2.4.10.17.1 Electrical Power Usage Report

2.4.10.17.2 Electrical Peak Demand Prediction Report

2.4.10.17.3 Energy usage Report

2.4.10.17.4 Water Usage Report

2.4.10.17.5 Alarm Report

2.4.10.17.6 M&C Software Override Report

2.4.10.17.7 Run Time Reports

2.4.10.17.8 Cooling Tower Profiles

2.4.10.17.9 Chiller usage Report

2.4.10.17.10 Device Offline Report

2.5 UNINTERRUPTIBLE POWER SUPPLY (UPS)

2.6 RACKS AND ENCLOSURES

2.6.1 Enclosures

2.6.1.1 Outdoors

2.6.1.2 Mechanical and Electrical Rooms

2.6.1.3 Other Locations

2.6.2 Equipment Racks

PART 3 EXECUTION

3.1 FACTORY TEST

3.2 EXISTING CONDITIONS SURVEY

3.3 DRAWINGS AND CALCULATIONS

3.3.1 UMCS IP Network Bandwidth Usage Estimate

3.3.2 Certificate of Networthiness Documentation

3.3.3 UMCS Contractor Design Drawings

3.3.4 As-Built Drawings

3.4 INSTALLATION REQUIREMENTS

3.4.1 General

3.4.2 Isolation, Building Penetrations and Equipment Clearance

3.4.3 Nameplates

3.5 INSTALLATION OF EQUIPMENT

3.5.1 Wire and Cable Installation

3.5.2 Grounding

3.5.3 Power-Line Surge Protection

3.5.4 IP Addresses

3.5.5 Computer Hardware and Software

3.5.5.1 Hardware Installation

3.5.5.2 Software Installation

3.5.5.3 Monitoring and Control (M&C) Software Configuration

3.5.5.4 Control Hardware Installation

3.6 INTEGRATION OF FIELD CONTROL SYSTEMS

3.6.1 Integration Step 1: Install Control Hardware

3.6.1.1 Installation of Control Protocol Gateway

3.6.1.2 Installation of Niagara Framework Supervisory Gateway

3.6.1.3 Installation of Control Protocol Router

3.6.1.4 Installation of BACnet Supervisory Controller

3.6.2 Integration Step 2: Add Field Control System to M&C Software

3.6.2.1 Integration of Field Control Systems Via ANSI-709.1-C

3.6.2.2 Integration of Field Control Systems Via ASHRAE 135

3.6.2.3 Integration of Field Control Systems Via Niagara Framework

3.6.2.4 Integration of Field Control Systems Via Modbus

3.6.2.5 Integration of Field Control Systems Via OPC DA

3.6.2.6 [Enter Appropriate Subpart Title Here]

SECTION 25 10 10 Page 5

3.6.3 Integration Step 3: Configure M&C Software

3.6.3.1 Configure M&C Software Communication

3.6.3.2 Configure M&C Software Functionality

3.7 START-UP AND START-UP TESTING

3.8 PERFORMANCE VERIFICATION TEST (PVT)

3.8.1 PVT Phase I Procedures

3.8.2 PVT Phase I

3.8.3 PVT Phase II

3.9 MAINTENANCE AND SERVICE

3.9.1 Work Coordination

3.9.2 Work Control

3.9.3 Working Hours

3.9.4 Equipment Repairs

3.9.5 Replacement, Modernization, Renovation

3.9.6 Access To UMCS Equipment

3.9.7 Records, Logs, and Progress Reports

3.9.8 Preventive Maintenance Requirements

3.9.8.1 Preventive Maintenance Work Plan

3.9.8.2 Semiannual Maintenance

3.9.8.3 Maintenance Procedures

3.9.8.3.1 Maintenance Coordination

3.9.8.3.2 Software/Firmware

3.9.8.3.3 Network

3.9.9 Service Call Reception

3.9.10 Service Call Work Warranty

3.9.11 System Modifications

3.10 TRAINING

3.10.1 Training Documentation

3.10.1.1 Course Attendance List

3.10.1.2 Training Manuals

3.10.2 Basic Training

3.10.3 Advanced Training

3.10.4 Refresher Training

ATTACHMENTS:

QC Checklist

-- End of Section Table of Contents --

SECTION 25 10 10 Page 6

**************************************************************************

USACE / NAVFAC / AFCEC / NASA UFGS-25 10 10 (February 2019)

-----------------------------

Preparing Activity: USACE Superseding

UFGS-25 10 10 (November 2015)

UNIFIED FACILITIES GUIDE SPECIFICATIONS

References are in agreement with UMRL dated July 2019

**************************************************************************

SECTION 25 10 10

UTILITY MONITORING AND CONTROL SYSTEM (UMCS) FRONT END AND INTEGRATION

02/19

**************************************************************************

NOTE: This guide specification covers the

requirements for a Utility Monitoring and Control

System (UMCS) Front End using Open protocols

(LonWorks, BACnet, Modbus, DNP and OPC), a UMCS

using the Niagara Framework, and the integration of

field control systems.

This specification includes tailoring options to

select the protocol(s) required to be supported at

the Monitoring and Controls Software (Front-end).

Note that unselected protocols can be integrated

through the use of a gateway.

This guide specification also includes tailoring

options for service-specific requirements for the

Air Force, Army and Navy as well as a "Service

Generic" tailoring option for use on other

projects. In order for this specification to be

properly tailored one (and only one) of the services

tailoring options (Air Force, Army, Navy, Service

Generic) must be selected.

Adhere to UFC 1-300-02 Unified Facilities Guide

Specifications (UFGS) Format Standard when editing

this guide specification or preparing new project

specification sections. Edit this guide

specification for project specific requirements by

adding, deleting, or revising text. For bracketed

items, choose applicable item(s) or insert

appropriate information.

Remove information and requirements not required in

the specific project, whether or not brackets are

present.

Comments, suggestions and recommended changes for

this guide specification are welcome and should be

submitted as a Criteria Change Request (CCR). CCRs

for this specification can be submitted through the

Whole Building Design Guide page for this section:

SECTION 25 10 10 Page 7

http://www.wbdg.org/ffc/dod/unified-facilities-guide-specifications-ufgs/ufgs-**************************************************************************

PART 1 GENERAL

**************************************************************************

NOTE: Use of this UFGS, and the UMCS design, must be

in accordance with UFC 3-470-01 Utility Monitoring

and Control System (UMCS) Front End and

Integration. The release process for UFCs is longer

than for UFGS. Once released UFC 3-470-01 will be

available online at

http://www.wbdg.org/

Note that the previous (outdated) version of the UFC

contains "LonWorks" in the title and should not be

used.

Template Points Schedules in electronic format for

use with this section are available online at the

Whole Building Design Guide page for this section:

http://www.wbdg.org/ffc/dod/unified-facilities-guide-specifications-ufgs/ufgs-**************************************************************************

**************************************************************************

NOTE: NOTE ON THE USE OF THIS SECTION WITH OTHER

SECTION. When using this Section on the same

project with specifications for building control

systems (Section 23 09 00 INSTRUMENTATION AND

CONTROL FOR HVAC, 23 09 23.01 LONWORKS DIRECT

DIGITAL CONTROL FOR HVAC AND OTHER BUILDING CONTROL

SYSTEMS, 23 09 23.02 BACNET DIRECT DIGITAL CONTROL

FOR HVAC AND OTHER BUILDING CONTROL SYSTEMS) there

may requirements that appear at first to be

conflicting but which are actually designed to be

complementary.

For example, Section 23 09 00 INSTRUMENTATION AND

CONTROL FOR HVAC excludes a front end while this

section (Section 25 10 10) requires a front end -

this is to avoid getting multiple front ends.

**************************************************************************

**************************************************************************

NOTE: This specification makes use of SpecsIntact

Tailoring Options. This note describes these

options and how to use them.

"TAILORING OPTION NOTES" Tailoring Option

Each time tailoring options are used there is an

accompanying designer note describing the text that

is tailored. As this Section makes heavy use of

tailoring options there are many of these notes and

they can distract from designer notes describing

other decisions. The designer notes describing

tailoring options are all in a "TAILORING OPTION

NOTES" tailoring option which can be hidden (in

SpecsIntact select View-Tailoring Options and then

SECTION 25 10 10 Page 8

deselect "TAILORING OPTION NOTES") once this section

is tailored and the tailoring option notes are no

longer needed.

Protocol Tailoring Options

This specification includes tailoring options for

selection of protocol, and whether the Niagara

Framework is required. There are five tailoring

options:

1) BACNET: A (non-Niagara Framework) BACnet

front end (using a BACnet B-AWS)

2) LONWORKS: A LonWorks front end using LNS.

3) NIAGARA FRAMEWORK: A Niagara Framework

front end

4) MODBUS: The front end must also support the

MODBUS protocol.

5) OPC: The front end must also support OPC.

In general, it is recommended that only one of

BACNET, LONWORKS or NIAGARA FRAMEWORK be selected.

It is also recommended neither MODBUS and OPC be

selected with BACNET.

You have currently selected the following options:

----------

BACNET

LONWORKS

NIAGARA FRAMEWORK

MODBUS

OPC

----------

If you don't see any text between dashes above, you

have deselected all of the protocol tailoring

options and this specification is not valid. Select

at least one of the tailoring options.

If you see more than one line of text between the

dashes above you have left multiple tailoring

options related to protocol selected. This may

result in conflicting requirements. See UFC

3-470-01 UTILITY MONITORING AND CONTROL SYSTEM

(UMCS) FRONT END AND INTEGRATION to determine if one

or more tailoring options should be deselected.

Service Tailoring Option

This specification also includes tailoring options

for the Service (Air Force, Army, Navy) the

specification is used for. There is a "Service

Generic" tailoring option that can also be used.

Only ONE of the four tailoring options related to

the services should be used. You have currently

selected the following options:

----------

AIR FORCE

SECTION 25 10 10 Page 9

ARMY

NAVY

SERVICE GENERIC

-----------

If more than one item appears between the dashes

above you have left more than one services tailoring

options selected and need to deselect all but one of

them.

**************************************************************************

**************************************************************************

NOTE: WARNING - The BACNET tailoring option has

been selected with another protocol tailoring option

(LONWORKS, MODBUS, NIAGARA FRAMEWORK). As described

in UFC 3-470-01, many of the Monitoring and Control

Software packages which support BACnet support ONLY

BACnet, so the inclusion of other protocol tailoring

options may unnecessarily limit the number of

vendors able to provide the UMCS. The need for

supporting multiple protocols at the Monitoring and

Control Software should be verified/checked with the

project site. Note that any protocol can be

integrated to the UMCS with the use of a gateway, so

omitting a tailoring option does not prohibit the

integration of systems using that protocol.

See UFC 3-470-01 for more information.

**************************************************************************

**************************************************************************

NOTE: WARNING - The NIAGARA FRAMEWORK tailoring

option has been selected with the LONWORKS tailoring

option. As described in UFC 3-470-01, LNS-based

LonWorks (required by the LONWORKS tailoring option)

is generally not compatible with the Niagara

Framework.

**************************************************************************

1.1 SUMMARY

**************************************************************************

NOTE: Designer must add location and site specific

requirements.

**************************************************************************

**************************************************************************

NOTE: This subpart uses tailoring options:

The sentence referring to only UFGS 23 09 23.01 will

be included if the LONWORKS tailoring options is

selected.

The sentence referring to only UFGS 23 09 23.02 will

be included if the BACNET tailoring option is

selected.

The sentence referring to both UFGS 23 09 23.01 and

UFGS 23 09 23.02 will be included if the NIAGARA

SECTION 25 10 10 Page 10

FRAMEWORK tailoring option is selected.

**************************************************************************

Provide a Utility Monitoring and Control System (UMCS) which performs

supervisory monitoring and supervisory control of base-wide building

control systems and utility control systems using one or more of:

CEA-709.1-D (LonWorks) with LonWorks Network Services (LNS), ASHRAE 135

(BACnet), MODBUS Protocol, MODBUS TCP/IP, OPC DA, or the Niagara Framework

with Fox protocol as indicated and shown. Integrate CEA-709.1-D field

control systems installed per Section 23 09 23.01 LONWORKS DIRECT DIGITAL

CONTROL FOR HVAC AND OTHER BUILDING CONTROL SYSTEMS into the UMCS as

specified and maintain the LNS database(s) for the entire network at the

UMCS Front End. Integrate field control systems installed per Section

23 09 23.01 LONWORKS DIRECT DIGITAL CONTROL FOR HVAC AND OTHER BUILDING

CONTROL SYSTEMS or Section 23 09 23.02 BACNET DIRECT DIGITAL CONTROL FOR

HVAC AND OTHER BUILDING CONTROL SYSTEMS to the UMCS via Niagara Framework

Supervisory Gateways as specified. Integrate ASHRAE 135 (BACnet) field

control systems installed per Section 23 09 23.02 BACNET DIRECT DIGITAL

CONTROL FOR HVAC AND OTHER BUILDING CONTROL SYSTEMS as specified.

1.1.1 System Requirements

**************************************************************************

NOTE: Select the appropriate text in the type

specific communication system requirements to

indicate whether or not the IP network will be

Government furnished. If the IP network is *not*

Government furnished be sure to include complete

requirements for the IP network in the contract

package. This specification does not provide

sufficient requirements for the procurement of an IP

network.

Use "[an IP network as specified in [_____] and ]"

only if the contractor is expected to install an IP

network. In this case provide the information on

the specification for the IP network in the

"[_____]" provided.

For Army, coordinate with the installation (DPW and

NEC) but the default selection will be "[the

Government furnished IP network]"

**************************************************************************

Provide a UMCS as specified and indicated, and in accordance with the

following characteristics:

1.1.1.1 General System Requirements

a. The system performs supervisory monitoring and control functions

including but not limited to Scheduling, Alarm Handling, Trending,

Overrides, Report Generation, and Electrical Demand Limiting as

specified.

b. The system includes a Graphical User Interface which allows for

graphical navigation between systems, graphical representations of

systems, access to real-time data for systems, ability to override

points in a system, and access to all supervisory monitoring and

control functions.

SECTION 25 10 10 Page 11

c. All software used by the UMCS and all software used to install and

configure the UMCS is licensed to and delivered to the installation.

d. All necessary documentation, configuration information, configuration

tools, programs, drivers, and other software is licensed to and

otherwise remains with the Government such that the Government or

their agents are able to repair, replace, upgrade, and expand the

system without subsequent or future dependence on the Contractor.

Software licenses must not require periodic fees and must be valid in

perpetuity.

e. Provide sufficient documentation and data, including rights to

documentation and data, such that the Government or their agents can

execute work to repair, replace, upgrade, and expand the system

without subsequent or future dependence on the Contractor.

f. The UMCS interfaces directly to ASHRAE 135, CEA-709.1-D,

MODBUS Protocol, MODBUS TCP/IP, OPC DA, and Niagara Framework field

control systems as specified and may interface to field control

systems using other protocols via an M&C Software protocol driver or a

Gateway.

g. For UMCS systems with Monitoring and Control Software functionality

implemented in Monitoring and Control (M&C) Controller Hardware,

provide sufficient additional controller hardware to support the full

capacity requirements as specified.

**************************************************************************

NOTE: The following TWO list paragraphs are

included only when the NIAGARA FRAMEWORK tailoring

option is selected.

**************************************************************************

h. All Niagara Framework components have an unrestricted interoperability

license with a Niagara Compatibility Statement (NiCS) following the

Tridium Open NiCS Specification and have a value of "ALL" for "Station

Compatibility In", "Station Compatibility Out", "Tool Compatibility

In" and "Tool Compatibility Out". Note that this will result in the

following entries in the license.dat file:

accept.station.in="*"

accept.station.out="*"

accept.wb.in="*"

accept.wb.out="*"

**************************************************************************

NOTE: Select the required version of the Niagara

Framework. This choice must be carefully

coordinated with the project site.

Niagara Framework is currently (2015) in a

transition between two releases: "AX" and "Version

4". A Version 4 UMCS front end (e.g. as specified

in Section 25 10 10) will work with either an AX or

Version 4 Niagara Framework Supervisory Gateway, but

an AX front end will ONLY work with an AX Niagara

Framework Supervisory Gateway.

If this Section is being used to procure a new front

SECTION 25 10 10 Page 12

end AND sufficient local support for Version 4

exist, keep the bracketed text to require Version

4. Otherwise, if this section is being used for

integration OR if there is insufficient local

support to allow requiring Version 4 remove the

bracketed text allow either Version 4 or AX.

**************************************************************************

[ i. The version of Niagara Framework used on this project must be Version

4.0 or later.]

1.1.1.2 LonWorks Requirements

**************************************************************************

NOTE: This subpart is only included when the

LONWORKS tailoring option is selected.

**************************************************************************

a. The UMCS must communicate using CEA-709.1-D over [the Government

furnished IP network] [an IP network as specified in [_____] and ][the

Navy PSNet] in accordance with CEA-852-C as specified and must

interface to CEA-709.1-D building control networks using LonWorks/IP

Routers as specified.

b. All communication between the UMCS and LonWorks field control networks

must be via the CEA-709.1-D protocol over the IP network in accordance

with CEA-852-C.

c. Except for communication for device commissioning, configuration, and

programming, all communication between the M&C Software and the field

control system devices must be via SNVT.

1.1.1.3 BACnet Requirements

**************************************************************************

NOTE: This subpart is only included when the BACNET

tailoring option is selected.

In addition, the reference to the Navy PSNet is

included only when the NAVY tailoring option is

selected.

**************************************************************************

a. The UMCS must communicate using ASHRAE 135 Annex J over [the

Government furnished IP network][an IP network as specified in [_____]

and ][the Navy PSNet] as specified.

b. All communication between the UMCS and ASHRAE 135 field control

networks must be via the ASHRAE 135 protocol over the IP network.

c. All communication between the M&C Software and the field control

system devices must be via standard ASHRAE 135 services other than

PrivateTransfer and ConfirmedPrivateTransfer except as follows:

(1) PrivateTransfer and ConfirmedPrivateTransfer may be used for

device configuration and device programming.

(2) PrivateTransfer and ConfirmedPrivateTransfer may be used for

communication between the M&C Software and the field control

SECTION 25 10 10 Page 13

system if and only if both the M&C Software and the field control

system devices automatically (without requiring reconfiguration)

revert to the use of other standard ASHRAE 135 services when one

of the components is modified or replaced.

1.1.1.4 Modbus Requirements

**************************************************************************

NOTE: This subpart is included only when the MODBUS

tailoring option is selected.

In addition, the reference to the Navy PSNet is

included only when the NAVY tailoring option is

selected.

**************************************************************************

The UMCS must communicate using MODBUS Protocol, MODBUS TCP/IP over [the

Government furnished IP network] [an IP network as specified in [_____]

and ][the Navy PSNet] as specified.

Modbus communications must support all of the following Modbus data types:

**************************************************************************

NOTE: FYI - the four standard data types in Modbus

are:

1) Discrete Input - a single bit (read only)

2) Coil - a single bit

3) Input Register - 16 bit (read only)

4) Holding Register - 16 bit

The Modbus standard does not define how the data is

interpreted. For example it does not say if the 16

bits from a Holding register are 16 different binary

flags, or an integer, or two ASCII characters or

something else entirely. The below requirements

specify how to format data for some common data

types.

**************************************************************************

a. The four standard data types defined by MODBUS Protocol, MODBUS TCP/IP:

Discrete Inputs, Coils, Input Registers, and Holding Registers. (Note

that these four data types are included in the MODBUS Protocol,

MODBUS TCP/IP standard. The remaining data types indicated in this

Section are not included in the MODBUS Protocol, MODBUS TCP/IP

standard but are defined by this Section to provide a standard for

communication between systems.)

b. Character: Character data using a single Input Register or single

Holding Register where that Modbus register is interpreted as two 8

bit ISO 8859-1 characters, with the low order bits representing the

right-hand character.

c. Floating Point: Floating point data using two consecutive Input

Registers or two consecutive Holding Registers where the resulting 32

bits are interpreted as a Binary32 (Single Precision Floating point)

number as specified in IEEE 754. Use the first Register for the

higher 16 bits, and the second Register for the lower 16 bits.

d. Integer Date: Date data using three consecutive Input Registers or

SECTION 25 10 10 Page 14

three consecutive Holding Registers where the resulting 48 bits are

interpreted as a 48-bit unsigned big-endian integer. The value is the

number of milliseconds, not including leap seconds, from

1970-01-01T00:00:00.000 (12AM, January 1, 1970). Use the first

Register for the highest 16 bits and the third Register for the lowest

16 bits.

e. Character Date: Date data using the format specified in ISO 8601 of

"YYYY-MM-DDTHH:MM:SS.SSS", where the individual characters are

formatted as specified for character data.

1.1.1.5 OPC Requirements

**************************************************************************

NOTE: This subpart is included only when the OPC

tailoring option is selected.

**************************************************************************

The UMCS must communicate using OPC DA over [the Government furnished IP

network] [an IP network as specified in [_____] and ][the Navy PSNet] as

shown and specified.

1.1.1.6 Niagara Framework Requirements

**************************************************************************

NOTE: This subpart is included only when the

NIAGARA FRAMEWORK tailoring option is selected.

In addition, this subpart used services tailoring

options:

1) the reference to the Navy PSNet is included only

when the NAVY tailoring option is selected.

2) The HTTP requirement is bracketed when the AIR

FORCE, ARMY or SERVICE GENERIC tailoring options are

selected.

**************************************************************************

**************************************************************************

NOTE: For the Navy, keep the bracketed text "and

HTTP".

For other services keep the bracketed text "and

HTTP" if the Niagara Framework Supervisory Gateways

will be permitted to serve web pages. Remove the

bracketed text "and HTTP" otherwise.

In general, for the Army remove the "and HTTP" text.

**************************************************************************

The UMCS must use the Niagara Framework and must communicate with

Niagara Framework field control systems using the Fox protocol[ and HTTP]

over [the Government furnished IP network] [an IP network as specified in

[_____] and ][the Navy PSNet] as indicated and specified.

[1.1.2 General Cybersecurity Requirements

**************************************************************************

NOTE: This subpart uses tailoring options so

include the Air Force document reference only when

SECTION 25 10 10 Page 15

the AIR FORCE tailoring option is selected and the

Army document reference when the ARMY tailoring

option is selected.

**************************************************************************

**************************************************************************

NOTE: The following paragraph provides a place to

include general system-level Cybersecurity

requirements above and beyond the requirements

already incorporated into the Product and Execution

parts of this specification. This paragraph may or

may not be required depending on how Information

Assurance is being addressed for the project and

site.

Provide specific requirements for Cybersecurity -

simply incorporating the references through the use

of the default test is generally NOT sufficient.

Cybersecurity requirements for Army systems should

be coordinated with the UMCS MCX.

**************************************************************************

Address cybersecurity in accordance with [AF ETL 11-1][DA AR 25-2][____].

]1.1.3 Symbols, Definition and Abbreviations

Use symbols, definitions, and engineering unit abbreviations indicated in

the contract drawings for displays, submittals and reports. For symbols,

definitions and abbreviations not in the contract drawings use terms

conforming at a minimum to IEEE Stds Dictionary and the ASHRAE FUN SI

ASHRAE FUN IP, as applicable.

1.1.4 System Units and Accuracy

**************************************************************************

NOTE: Accuracy of calculations and precision and

resolution of displays for the UMCS is specified in

terms of the accuracy of the sensors used in the

building controls connected to the UMCS. Edit the

brackets to indicate a reference to UFGS 23 09 00

INSTRUMENTATION AND CONTROL FOR HVAC to reference a

different specification, or to include accuracy

requirements.

**************************************************************************

Use [metric (SI)] [English (inch-pound)] units for displays, print-outs

and calculations. Perform calculations with an accuracy of at least three

significant figures. For displays and printouts present values to at

least three significant figures.

1.1.5 Data Packages/Submittals Requirements

**************************************************************************

NOTE: Coordinate the review of all submittals with

the project site. The site may have a System

Integrator or other individual/office that should

review all submittals before acceptance of the

SECTION 25 10 10 Page 16

system.

The acquisition of all technical data, data bases

and computer software items that are identified

herein will be accomplished strictly in accordance

with the Federal Acquisition Regulation (FAR) and

the Defense Acquisition Regulation Supplement

(DFARS). Those regulations as well as the Services

implementations thereof should also be consulted to

ensure that a delivery of critical items of

technical data is not inadvertently lost.

Specifically, DFARS 252.227-7013 Rights in Technical

Data - Noncommercial Items as well as any requisite

software licensing agreements will be made a part of

the CONTRACT CLAUSES or SPECIAL CONTRACT

REQUIREMENTS.

In addition, the appropriate DD Form 1423 Contract

Data Requirements List, will be filled out for each

distinct deliverable data item and made a part of

the contract. Where necessary, a DD Form 1664, Data

Item Description, will be used to explain and more

fully identify the data items listed on the DD Form

1423. It is to be noted that all of these clauses

and forms are required to ensure the delivery of the

data in question and that such data is obtained with

the requisite rights to use by the Government.

Include with the request for proposals a completed

DD Form 1423, Contract Data Requirements List. This

form is essential to obtain delivery of all

documentation. Each deliverable will be clearly

specified, both description and quantity being

required.

**************************************************************************

Technical data packages consisting of computer software and technical data

(meaning technical data which relates to computer software) which are

specifically identified in this project and which may be defined/required

in other specifications must be delivered strictly in accordance with the

CONTRACT CLAUSES and in accordance with the Contract Data Requirements

List, DD Form 1423. Data delivered must be identified by reference to the

particular specification paragraph against which it is furnished. All

submittals not specified as technical data packages are considered shop

drawings under the Federal Acquisition Regulation Supplement (FARS) and

must contain no proprietary information and must be delivered with

unrestricted rights.

1.2 REFERENCES

**************************************************************************

NOTE: This paragraph is used to list the

publications cited in the text of the guide

specification. The publications are referred to in

the text by basic designation only and listed in

this paragraph by organization, designation, date,

and title.

Use the Reference Wizard's Check Reference feature

SECTION 25 10 10 Page 17

when you add a RID (Reference ID) outside of the

Section's Reference Article to automatically place

the reference in the Reference Article. Also use

the Reference Wizard's Check Reference feature to

update the issue dates.

References not used in the text will automatically

be deleted from this section of the project

specification when you choose to reconcile

references in the publish print process.

**************************************************************************

The publications listed below form a part of this specification to the

extent referenced. The publications are referred to within the text by

the basic designation only.

AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI)

ANSI INCITS 154 (1988; R 2004) Office Machines and

Supplies - Alphanumeric Machines -

Keyboard Arrangement

AMERICAN SOCIETY OF HEATING, REFRIGERATING AND AIR-CONDITIONING

ENGINEERS (ASHRAE)

ASHRAE 135 (2016) BACnet—A Data Communication

Protocol for Building Automation and

Control Networks

ASHRAE FUN IP (2017) Fundamentals Handbook, I-P Edition

ASHRAE FUN SI (2017) Fundamentals Handbook, SI Edition

CONSUMER ELECTRONICS ASSOCIATION (CEA)

CEA-709.1-D (2014) Control Network Protocol

Specification

CEA-709.3 (1999; R 2015) Free-Topology Twisted-Pair

Channel Specification

CEA-852-C (2014) Tunneling Device Area Network

Protocols Over Internet Protocol Channels

INSTITUTE OF ELECTRICAL AND ELECTRONICS ENGINEERS (IEEE)

IEEE 754 (2008) Floating-Point Arithmetic - IEEE

Computer Society

IEEE 802.11 (2016; AI 2017; AJ 2018; AK 2018; AQ 2018)

Information Technology-Telecommunications

and Information Exchange Between Systems

Local and Metropolitan Area

Networks-Specific Requirements Part 11:

Wireless LAN Medium Access Control (MAC)

and Physical Layer (PHY) Specifications

IEEE 1815 (2015; CORR 2016) Exchanging Information

Between Networks Implementing IEC 61850

SECTION 25 10 10 Page 18

and IEEE Std 1815 [Distributed Network

Protocol (DNP3)]

IEEE C62.41 (1991; R 1995) Recommended Practice on

Surge Voltages in Low-Voltage AC Power

Circuits

IEEE Stds Dictionary (2009) IEEE Standards Dictionary: Glossary

of Terms & Definitions

INTERNATIONAL ORGANIZATION FOR STANDARDIZATION (ISO)

ISO 8601 (2004) Data Elements and Interchange

Formats - Information Interchange -

Representation of Dates and Times

ISO 8859-1 (1998) Information Technology - 8-Bit

Single-Byte Coded Graphic Character Sets -

Part 1: Latin Alphabet No. 1

INTERNET ENGINEERING TASK FORCE (IETF)

IETF RFC 4361 (2006) Node-specific Client Identifiers

for Dynamic Host Configuration Protocol

Version Four (DHCPv4)

IETF RFC 7465 (2015) Prohibiting RC4 Cipher Suites

RFC 821 (2001) Simple Mail Transfer Protocol (SMTP)

LONMARK INTERNATIONAL (LonMark)

LonMark Interoperability Guide (2005) LonMark Application-Layer

Interoperability Guide and LonMark Layer

1-6 Interoperability Guide; Version 3.4

LonMark SNVT List (2014) LonMark SNVT Master List; Version 15

LonMark XIF Guide (2001) LonMark External Interface File

Reference Guide; Revision 4.402

MODBUS ORGANIZATION, INC (MODBUS)

MODBUS Protocol (2012) Modbus Application Protocol

Specification; Version 1.1b3

MODBUS TCP/IP (2006) Modbus Messaging on TCP/IP

Implementation Guide; Version V1.0b

NATIONAL ELECTRICAL MANUFACTURERS ASSOCIATION (NEMA)

NEMA 250 (2018) Enclosures for Electrical Equipment

(1000 Volts Maximum)

NATIONAL FIRE PROTECTION ASSOCIATION (NFPA)

NFPA 70 (2017; ERTA 1-2 2017; TIA 17-1; TIA 17-2;

TIA 17-3; TIA 17-4; TIA 17-5; TIA 17-6;

TIA 17-7; TIA 17-8; TIA 17-9; TIA 17-10;

SECTION 25 10 10 Page 19

TIA 17-11; TIA 17-12; TIA 17-13; TIA

17-14; TIA 17-15; TIA 17-16; TIA 17-17 )

National Electrical Code

NFPA 262 (2019) Standard Method of Test for Flame

Travel and Smoke of Wires and Cables for

Use in Air-Handling Spaces

OPC FOUNDATION (OPC)

OPC DA (Ver 3.0; Errata) OPC Data Access (DA)

TELECOMMUNICATIONS INDUSTRY ASSOCIATION (TIA)

TIA-568-C.1 (2009; Add 2 2011; Add 1 2012) Commercial

Building Telecommunications Cabling

Standard

TIA-606 (2017c) Administration Standard for the

Telecommunications Infrastructure

TIA-607 (2015c; Addendum 1 2017) Generic

Telecommunications Bonding and Grounding

(Earthing) for Customer Premises

TRIDIUM, INC (TRIDIUM)

Niagara Framework (2012) Niagara 4 User's Guide

Tridium Open NiCS (2005) Understanding the Niagara 4

Compatibility Statement (NiCS)

U.S. AIR FORCE (USAF)

AF ETL 11-1 (2011) Civil Engineer Industrial Control

System Information Assurance Compliance

U.S. ARMY (DA)

DA AR 25-2 (2007; RAR 2009) Information Assurance

U.S. FEDERAL COMMUNICATIONS COMMISSION (FCC)

FCC EMC (2002) FCC Electromagnetic Compliance

Requirements

FCC Part 15 Radio Frequency Devices (47 CFR 15)

UNDERWRITERS LABORATORIES (UL)

UL 1778 (2014; Reprint Sep 2017) UL Standard for

Safety Uninterruptible Power Systems

UL 60950 (2000; Reprint Oct 2007) Safety of

Information Technology Equipment

1.3 DEFINITIONS

The following list of definitions may contain terms not found elsewhere in

SECTION 25 10 10 Page 20

this Section but are included here for completeness. Some terms are

followed with a protocol reference in parenthesis indicating to which

protocol the term and definition applies. Inclusion of protocol-specific

definitions does not create a requirement to support that protocol, nor

does it relax any requirements to support specific protocols as indicated

elsewhere in this section.

1.3.1 Alarm Generation

The process of comparing a point value (the point being alarmed) with a

pre-defined alarm condition (e.g. a High Limit) and performing some action

based on the result of the comparison.

1.3.2 Alarm Handling

see Alarm Routing

1.3.3 Alarm Routing

Alarm routing is M&C software functionality that starts with a

notification that an alarm exists (typically as the output of an Alarm

Generation process) and sends a specific message to a specific alarm

recipient or device.

1.3.4 Application Generic Controller (AGC)(LonWorks)

A device that is furnished with a (limited) pre-established application

that also has the capability of being programmed. Further, the ProgramID

and XIF file of the device are fixed. The programming capability of an AGC

may be less flexible than that of a General Purpose Programmable

Controller (GPPC).

1.3.5 Application Specific Controller (ASC)(LonWorks)

A device that is furnished with a pre-established built in application

that is configurable but not re-programmable. An ASC has a fixed

factory-installed application program (i.e Program ID) with configurable

settings.

1.3.6 BACnet (BACnet)

The term BACnet is used in two ways. First meaning the BACnet Protocol

Standard - the communication requirements as defined by ASHRAE 135

including all annexes and addenda. The second to refer to the overall

technology related to the ASHRAE 135 protocol.

1.3.7 BACnet Advanced Application Controller (B-AAC)(BACnet)

A hardware device BTL Listed as a B-AAC. A control device which contains

BIBBs in support of scheduling and alarming but otherwise has limited

resources relative to a B-BC. It may be intended for specific applications

and supports some degree of programmability.

1.3.8 BACnet Advanced Operator Workstation (B-AWS)(BACnet)

Monitoring and Control (M&C) Software BTL Listed as an Advanced Operator

Workstation and includes the ability to manage scheduling, alarming and

trending in an open manner. The B-AWS is the advanced operator's window

into a BACnet system. It is primarily used to monitor the performance of a

SECTION 25 10 10 Page 21

system and to modify parameters that affect the operation of a system.

1.3.9 BACnet Application Specific Controller (B-ASC)(BACnet)

A hardware device BTL Listed as a B-ASC. A controller with limited

resources relative to a B-AAC. It is intended for use in a specific

application and supports limited programmability.

1.3.10 BACnet Building Controller (B-BC)(BACnet)

A hardware device BTL Listed as a B-BC. A general-purpose,

field-programmable device capable of carrying out a variety of building

automation and control tasks including control and monitoring via direct

digital control (DDC) of specific systems and data storage for trend

information, time schedules, and alarm data. Like the other BTL Listed

controller types (B-AAC, B-ASC etc.) a B-BC device is required to support

the server ("B") side of the ReadProperty and WriteProperty services, but

unlike the other controller types it is also required to support the

client ("A") side of these services. Communication between controllers

requires that one of them support the client side and the other support

the server side, so a B-BC is often used when communication between

controllers is needed.

1.3.11 BACnet Internetwork (BACnet)

Two or more BACnet networks connected with BACnet routers. In a BACnet

Internetwork, there exists only one message path between devices.

1.3.12 BACnet Interoperability Building Blocks (BIBBs) (BACnet)

A BIBB is a collection of one or more BACnet services intended to define a

higher level of interoperability. BIBBs are combined to build the BACnet

functional requirements for a device in a specification. Some BIBBs

define additional requirements (beyond requiring support for specific

services) in order to achieve a level of interoperability. For example,

the BIBB DS-V-A (Data Sharing-View-A), which would typically be used by an

M&C client, not only requires the client to support the ReadProperty

Service, but also provides a list of data types (Object / Properties)

which the client must be able to interpret and display for the user.

1.3.13 BACnet Operator Display (B-OD)(BACnet)

A hardware device BTL Listed as a B-OD. A basic operator interface with

limited capabilities relative to a B-OWS. It is not intended to perform

direct digital control. The B-OD profile could be used for wall-mounted

LCD devices, displays affixed to BACnet devices; hand-held terminals or

other very simple user interfaces.

1.3.14 BACnet Operator Workstation (B-OWS)(BACnet)

Monitoring and Control (M&C) Software BTL Listed as a B-OWS. An operator

interface with limited capabilities relative to a B-AWS. The B-OWS is

used for monitoring and basic control of a system, but differs from a

B-AWS in that it does not support configuration activities, nor does it

provide advanced troubleshooting capabilities.

1.3.15 BACnet Smart Actuator (B-SA)(BACnet)

A hardware device BTL Listed as a B-SA. A simple control output device

SECTION 25 10 10 Page 22

with limited resources; it is intended for specific applications.

1.3.16 BACnet Smart Sensor (B-SS)(BACnet)

A hardware device BTL Listed as a B-SS. A simple sensing device with very

limited resources.

1.3.17 BACnet Testing Laboratories (BTL)(BACnet)

Established by BACnet International to support compliance testing and

interoperability testing activities and consists of BTL Manager and the

BTL Working Group (BTL-WG). BTL also publishes Implementation Guidelines.

1.3.18 BACnet Testing Laboratories (BTL) Listed (BACnet)

A device that has been certified by BACnet® Testing Laboratory. Devices

may be certified to a specific device profile, in which case the

certification indicates that the device supports the required capabilities

for that profile, or may be certified as "other".

1.3.19 Binary

A two-state system or signal; for example one where an "ON" condition is

represented by a high signal level and an "OFF" condition is represented

by a low signal level. 'Digital' is sometimes used interchangeably with

'binary'.

1.3.20 Binding (LonWorks)

The act of establishing communications between CEA-709.1-D devices by

associating the output of a device to the input of another so that

information is automatically (and regularly) sent without being requested

by the recipient.

1.3.21 Broadcast

Unlike most messages, which are intended for a specific recipient device,

a broadcast message is intended for all devices on the network.

1.3.22 Building Control Network (BCN)

The network used by the Building Control System. Typically the BCN is a

BACnet ASHRAE 135 or LonWorks CEA-709.1-D network installed by the

building control system contractor.

1.3.23 Building Control System (BCS)

One type of Field Control System. A control system for building

electrical and mechanical systems, typically HVAC (including central

plants) and lighting. A BCS generally uses Direct Digital Control (DDC)

Hardware and generally does NOT include its own local front end.

1.3.24 Building Point of Connection (BPOC)

A FPOC for a Building Control System. (This term is being phased out of

use in preference for FPOC but is still used in some specifications and

criteria. When it was used, it typically referred to a piece of control

hardware. The current FPOC definition typically refers instead to IT

hardware)

SECTION 25 10 10 Page 23

1.3.25 Channel (LonWorks)

A portion of the control network consisting of one or more segments

connected by repeaters. Channels are separated by routers. The device

quantity limitation is dependent on the topology/media and device type.

For example, a TP/FT-10 network with locally powered devices is limited to

128 devices per channel.

1.3.26 Commandable (BACnet)

A point (Object) is commandable if its Present_Value Property is writable

and it supports the optional Priority_Array Property. This functionality

is useful for Overrides.

1.3.27 Configuration Property (LonWorks)

Controller parameter used by the application which is usually set during

installation/testing and seldom changed. For example, the P and I

settings of a P-I control loop. Also see 'Standard Configuration Property

Type (SCPT)'

1.3.28 Control Logic Diagram

A graphical representation of control logic for multiple processes that

make up a system.

1.3.29 Device Object (BACnet)

Every BACnet device requires one Device Object, whose properties represent

the network visible properties of that device. Every Device Object

requires a unique Object_Identifier number on the BACnet Internetwork.

This number is often referred to as the device instance or device ID.

1.3.30 Explicit Messaging (LonWorks)

A non-standard and often vendor (application) specific method of

communication between devices.

1.3.31 External Interface File (XIF) (LonWorks)

A file which documents a device's external interface, specifically the

number and types of LonMark objects, the number, types, directions, and

connection attributes of network variables, and the number of message tags.

1.3.32 Field Point Of Connection (FPOC)

The FPOC is part of the UMCS IP network and acts as the point of

connection between the UMCS IP Network and the field control IP network.

The FPOC is an IT device such as a switch, IP router, or firewall,

typically managed by the site IT staff. (Note that the field control IP

network may consist of a single IP device, or that integration may require

installation of a field control network IP device.)

1.3.33 Field Control Network

The network used by a field control system.

SECTION 25 10 10 Page 24

1.3.34 Field Control System (FCS)

A building control system or utility control system.

1.3.35 Fox Protocol (Niagara Framework)

The protocol used for communication between components in the Niagara

Framework. By default, Fox uses TCP port 1911

1.3.36 Functional Profile (LonWorks)

A standard description, defined by LonMark International, of a LonMark

Object used to classify and certify devices.

1.3.37 Gateway

A device that translates from one protocol to another. Devices that

change only the transport mechanism of the protocol - "translating" from

LonWorks over TP/FT-10 to LonWorks over IP for example - are not gateways

as the underlying protocol (data format) does not change. Gateways are

also called Communications Bridges or Protocol Translators.

1.3.38 General Purpose Programmable Controller (GPPC) (LonWorks)

Unlike an ASC or AGC, a GPPC is not furnished with a fixed application

program and does not have a fixed ProgramID or XIF file. A GPPC can be

(re-)programmed, usually using vendor-supplied software. When a change to

the program affects the external interface (and the XIF file) the

ProgramID will change.

1.3.39 Internetwork (BACnet)

See BACnet Internetwork.

1.3.40 JACE (Niagara Framework)

Java Application Control Engine. See Niagara Framework Supervisory Gateway

1.3.41 LonMark Object (LonWorks)

A collection of network variables, configuration properties, and

associated behavior defined by LonMark International and described by a

Functional Profile. It defines how information is exchanged between

devices on a network (inputs from and outputs to the network).

1.3.42 LNS Plug-in (LonWorks)

Software which runs in an LNS compatible software tool, typically a

network configuration tool. Device configuration plug-ins provide a 'user

friendly' method to edit a device's configuration properties.

1.3.43 LonMark (LonWorks)

See LonMark International. Also, a certification issued by LonMark

International to CEA-709.1-D devices.

1.3.44 LonMark International (LonWorks)

Standards committee consisting of independent product developers, system

SECTION 25 10 10 Page 25

integrators and end users dedicated to determining and maintaining the

interoperability guidelines for LonWorks. Maintains guidelines for the

interoperability of CEA-709.1-D devices and issues the LonMark

Certification for CEA-709.1-D devices.

1.3.45 LonWorks (LonWorks)

The term used to refer to the overall technology related to the CEA-709.1-D

protocol (sometimes called "LonTalk"), including the protocol itself,

network management, interoperability guidelines and products.

1.3.46 LonWorks Network Services (LNS) (LonWorks)

A network management and database standard for CEA-709.1-D devices.

1.3.47 LonWorks Network Services (LNS) Database (LonWorks)

The standard database created and used by LonWorks Network Services (LNS)

compatible tools, such as LNS Network Configuration tools.

1.3.48 Modbus

A basic protocol for control network communications generally used in

utility control systems. The Modbus protocol standard is maintained by

The Modbus Organization.

1.3.49 Master-Slave/Token Passing (MS/TP)(BACnet)

Data link protocol as defined by the BACnet standard. Multiple speeds

(data rates) are permitted by the BACnet MS/TP standard.

1.3.50 Monitoring and Control (M&C) Software

The UMCS 'front end' software which performs supervisory functions such as

alarm handling, scheduling and data logging and provides a user interface

for monitoring the system and configuring these functions.

1.3.51 Network (BACnet)

In BACnet, a portion of the control internetwork consisting of one or more

segments of the same media connected by repeaters. Networks are separated

by routers.

1.3.52 Network Variable (LonWorks)

See 'Standard Network Variable Type (SNVT)'.

1.3.53 Network Configuration Tool (LonWorks)

The software used to configure the control network and set device

configuration properties. This software creates and modifies the control

network database (LNS Database).

1.3.54 Niagara Framework

A set of hardware and software specifications for building and utility

control owned by Tridium Inc. and licensed to multiple vendors. The

Framework consists of front end (M&C) software, web based clients, field

level control hardware, and engineering tools. While the Niagara

SECTION 25 10 10 Page 26

Framework is not adopted by a recognized standards body and does not use

an open licensing model, it is sufficiently well-supported by multiple

HVAC vendors to be considered a de-facto Open Standard.

1.3.55 Niagara Framework Supervisory Gateway (Niagara Framework)

DDC Hardware component of the Niagara Framework. A typical Niagara

architecture has Niagara specific supervisory gateways at the IP level and

other (non-Niagara specific) controllers on field networks (TP/FT-10,

MS/TP, etc.) beneath the Niagara supervisory gateways. The Niagara

specific controllers function as a gateway between the Niagara framework

protocol (Fox) and the field network beneath. These supervisory gateways

may also be used as general purpose controllers and also have the

capability to provide a web-browser based user interface.

Note that different vendors refer to this component by different names.

The most common name is "JACE"; other names include "EC-BOS", "FX-40", and

"UNC".

1.3.56 Node (LonWorks)

A device that communicates using the CEA-709.1-D protocol and is connected

to a CEA-709.1-D network.

1.3.57 Node Address (LonWorks)

The logical address of a node on the network, consisting of a Domain

number, Subnet number and Node number. Note that the "Node number"

portion of the address is the number assigned to the device during

installation and is unique within a subnet. This is not the factory-set

unique Node ID (see Node ID).

1.3.58 Node ID (LonWorks)

A unique 48-bit identifier assigned (at the factory) to each CEA-709.1-D

device. Sometimes called the Neuron ID.

1.3.59 Object (BACnet)

A BACnet Object. The concept of organizing BACnet information into

standard components with various associated Properties. Examples include

Analog Input objects and Binary Output objects.

1.3.60 Override

To change the value of a point outside of the normal sequence of operation

where this change has priority over the sequence. An override can be

accomplished in one of two ways: the point itself may be Commandable and

written to with a priority or there may be a separate point on the

controller for the express purpose of implementing the override.

Typically this override is from the Utility Monitoring and Control System

(UMCS) Monitoring and Control (M&C) Software. Note that this definition

is not standard throughout industry.

1.3.61 Point, Calculated

A value within the M&C Software that is not a network point but has been

calculated by logic within the software based on the value of network

SECTION 25 10 10 Page 27

points or other calculated points. Calculated points are sometimes called

virtual points or internal points.

1.3.62 Point, Network

A value that the M&C Software reads from or writes to a field control

network.

1.3.63 Polling

A requested transmission of data between devices, rather than an

unrequested transmission such as Change-Of-Value (COV) or Binding where

data is automatically transmitted under certain conditions.

1.3.64 Program ID (LonWorks)

An identifier (number) stored in the device (usually EEPROM) that

identifies the node manufacturer, functionality of device (application &

sequence), transceiver used, and intended device usage.

1.3.65 Property (BACnet)

A BACnet Property - a data element associated with an Object. Different

Objects have different Properties, for example an Analog Input Object has

a Present_Value Property (which provides the value of the underlying

hardware analog input), a High_Limit Property (which contains a high limit

for alarming), as well as other properties.

1.3.66 Protocol Implementation Conformance Statement (PICS)(BACnet)

A document, created by the manufacturer of a device, which describes which

potions of the BACnet standard are implemented by a given device.

1.3.67 Repeater

A device that connects two control network segments and retransmits all

information received on one side onto the other.

1.3.68 Router (LonWorks)

A device that connects two channels and controls traffic between the

channels by retransmitting signals received from one subnet onto the other

based on the signal destination. Routers are used to subdivide a control

network and to control bandwidth usage.

1.3.69 Router (BACnet)

A device that connects two or more BACnet networks and controls traffic

between the networks by retransmitting signals received from one network

onto another based on the signal destination. Routers are used to

subdivide an internetwork and to control bandwidth usage.

1.3.70 Segment

A 'single' section of a control network that contains no repeaters or

routers. There is generally a limit on the number of devices on a

segment, and this limit is dependent on the topology/media and device

type. For example, a TP/FT-10 segment with locally powered devices is

limited to 64 devices, and a BACnet MS/TP segment is limited to 32 devices.

SECTION 25 10 10 Page 28

1.3.71 Service (BACnet)

A BACnet Service. A defined method for sending a specific type of data

between devices. Services are always defined in a Client-Server manner,

with a Client initiating a Service request and a Server Executing the

Service. Some examples are ReadProperty (a client requests a data value

from a server), WriteProperty (a client writes a data value to a server),

and CreateObject (a client requests that a server create a new object

within the server device).

1.3.72 Service Pin (LonWorks)

A hardware push-button on a device which causes the device to broadcast a

message containing its Node ID and Program ID. This broadcast can also be

initiated via software.

1.3.73 Standard BACnet Object/Property/Service (BACnet)

BACnet Objects, Properties, or Services that are standard Objects,

Properties, or Services enumerated and defined in ASHRAE 135. Clause 23

of ASHRAE 135 defines methods to extend ASHRAE 135 to non-standard or

proprietary information. Standard BACnet Objects/Properties/Services

specifically exclude any vendor specific extensions.

1.3.74 Standard Configuration Property Type (SCPT) (LonWorks)

Pronounced 'skip-it'. A standard format type (maintained by LonMark

International) for Configuration Properties.

1.3.75 Standard Network Variable Type (SNVT) (LonWorks)

Pronounced 'snivet'. A standard format type (maintained by LonMark

International) used to define data information transmitted and received by

the individual nodes. The term SNVT is used in two ways. Technically it

is the acronym for Standard Network Variable Type, and is sometimes used

in this manner. However, it is often used to indicate the network

variable itself (i.e. it can mean "a network variable of a standard

network variable type"). In general, the intended meaning should be clear

from the context.

1.3.76 Subnet (LonWorks)

Consists of a logical grouping of up to 127 nodes, where the logical

grouping is defined by node addressing. Each subnet is assigned a number

which is unique within the Domain. See also Node Address.

1.3.77 Supervisory Controller

A controller implementing a combination of supervisory logic (global

control strategies or optimization strategies), scheduling, alarming,

event management, trending, web services or network management. Note this

is defined by use; many supervisory controllers have the capability to

also directly control equipment.

1.3.78 Supervisory Gateway

**************************************************************************

NOTE: This subpart uses tailoring options: The

SECTION 25 10 10 Page 29

phrase ", such as a Niagara Framework Supervisory

Gateway" is only included when the NIAGARA FRAMEWORK

tailoring option is selectedT

**************************************************************************

A device that is both a supervisory controller and a gateway, such as a

Niagara Framework Supervisory Gateway.

1.3.79 TP/FT-10 (LonWorks)

A Free Topology Twisted Pair network (at 78 kbps) defined by CEA-709.3.

This is the most common media type for a CEA-709.1-D control network.

1.3.80 TP/XF-1250 (LonWorks)

A high speed (1.25 Mbps) twisted pair, doubly-terminated bus network

defined by the LonMark Interoperability Guidelines. This media is

typically used only as a backbone media to connect multiple TP/FT-10

networks.

1.3.81 UMCS Network

An IP network connecting multiple field control systems to the Monitoring

and Control Software using one or more of: LonWorks (CEA-709.1-D and

CEA-852-C), BACnet (ASHRAE 135 Annex J), MODBUS Protocol, MODBUS TCP/IP or

OPC DA.

1.3.82 User-defined Configuration Property Type (UCPT) (LonWorks)

Pronounced 'u-keep-it'. A Configuration Property format type that is

defined by the device manufacturer.

1.3.83 User-defined Network Variable Type (UNVT) (LonWorks)

A network variable format defined by the device manufacturer. Note that

UNVTs create non-standard communications (other vendor's devices may not

correctly interpret it) and may close the system and therefore are not

permitted by this specification.

1.3.84 Utility Control System (UCS)

One type of field control system. Used for control of utility systems

such as an electrical substation, sanitary sewer lift station, water pump

station, etc. Building controls are excluded from a UCS, however it is

possible to have a Utility Control System and a Building Control System in

the same facility, and for those systems to share components such as the

FPOC. A UCS may include its own local front-end.

1.4 SUBMITTALS

**************************************************************************

NOTE: Review submittal description (SD) definitions

in Section 01 33 00 SUBMITTAL PROCEDURES and edit

the following list to reflect only the submittals

required for the project. Submittals should be kept

to the minimum required for adequate quality control.

A “G” following a submittal item indicates that the

submittal requires Government approval. Some

SECTION 25 10 10 Page 30

submittals are already marked with a “G”. Only

delete an existing “G” if the submittal item is not

complex and can be reviewed through the Contractor’s

Quality Control system. Only add a “G” if the

submittal is sufficiently important or complex in

context of the project.

For submittals requiring Government approval on Army

projects, a code of up to three characters within

the submittal tags may be used following the "G"

designation to indicate the approving authority.

Codes for Army projects using the Resident

Management System (RMS) are: "AE" for

Architect-Engineer; "DO" for District Office

(Engineering Division or other organization in the

District Office); "AO" for Area Office; "RO" for

Resident Office; and "PO" for Project Office. Codes

following the "G" typically are not used for Navy,

Air Force, and NASA projects.

Choose the first bracketed item for Navy, Air Force

and NASA projects, or choose the second bracketed

item for Army projects.

**************************************************************************

**************************************************************************

NOTE: Coordinate the review of all submittals with

the project site. The site may have a Building

Automation System (BAS) Manager or other

individual/office that should review all submittals

before acceptance of the system.

**************************************************************************

Government approval is required for submittals with a "G" designation;

submittals not having a "G" designation are for [Contractor Quality

Control approval.] [information only. When used, a designation following

the "G" designation identifies the office that will review the submittal

for the Government.] Submittals with an "S" are for inclusion in the

Sustainability eNotebook, in conformance to Section 01 33 29

SUSTAINABILITY REPORTING. Submit the following in accordance with Section

01 33 00 SUBMITTAL PROCEDURES and TABLE 1: PROJECT SEQUENCING:

**************************************************************************

NOTE: The submittals included in this guide

specification are critical and require Government

review. Any added submittals normally should be for

information only and reviewed through the Contractor

Quality Control system.

**************************************************************************

SD-02 Shop Drawings

**************************************************************************

NOTE: Either indicate drawing size, or leave both

options to allow the contractor to decide.

When selecting format for electronic drawings

coordinate with the project site. Be sure to

require drawings in a format that is usable by the

SECTION 25 10 10 Page 31

site maintenance staff. This may require including

multiple format requirements here.

Indicate quantities for submittals.

**************************************************************************

UMCS Contractor Design Drawings; G[, [_____]]

UMCS Contractor Design Drawings as a single complete package:

[_____] hard copies and [_____] copies on CDROM. Submit hardcopy

drawings on [ISO A1 841 by 594 mm 34 by 22 inches][or][A3 420 by

297 mm 17 by 11 inches] sheets, and electronic drawings in both

PDF and [AutoCAD][Microstation][Bentley BIM V8][Autodesk Revit

2013] format.

Draft As-Built Drawings; G[, [_____]]

Draft As-Built Drawings as a single complete package: [_____]

hard copies and [_____] copies on CDROM. Submit hardcopy drawings

must on [ISO A1 841 by 594 mm 34 by 22 inches][or][A3 420 by 297 mm

17 by 11 inches] sheets, and electronic drawings in both PDF and

[AutoCAD][Microstation][Bentley BIM V8][Autodesk Revit 2013]

format.

Final As-Built Drawings; G[, [_____]]

Final As-Built Drawings as a single complete package: [_____]

hard copies and [_____] copies on CDROM. Submit hardcopy drawings

on [ISO A1 841 by 594 mm 34 by 22 inches][or][A3 420 by 297 mm 17

by 11 inches] sheets, and electronic drawings in both PDF and

[AutoCAD][Microstation][Bentley BIM V8][Autodesk Revit 2013]

format.

SD-03 Product Data

Product Data Sheets; G[, [_____]]

Computer Software; G[, [_____]]

The most recent versions of all computer software provided under

this specification delivered as a Technical Data Package. Submit

the user manuals for all software delivered for this project with

the software.

Enclosure Keys

**************************************************************************

NOTE: Certificate of Networthiness Documentation is

only required for Army projects and is only included

when the ARMY tailoring options is selected.

**************************************************************************

Certificate of Networthiness Documentation; G[, [_____]]

Documentation of existing Certificates of Networthiness or

completed Certificate of Networthiness "Application Checklist"

[via e-mail and ]on optical disc.

SD-05 Design Data

SECTION 25 10 10 Page 32

UMCS IP Network Bandwidth Usage Estimate; G[, [_____]]

[Four ][_____] copies of the UMCS IP Network Bandwidth Usage

Estimate.

SD-06 Test Reports

Pre-Construction QC Checklist; G[, [_____]]

[Four] [_____] copies of the Pre-Construction QC Checklist.

Post-Construction QC Checklist; G[, [_____]]

[Four] [_____] copies of the Post-Construction QC Checklist.

[

**************************************************************************

NOTE: If not requiring a Factory Test in PART 3

EXECUTION, remove the submittal requirements for

Factory Test Procedures and Factory Test Report

**************************************************************************

Factory Test Procedures; G[, [_____]]

[Four] [_____] copies of the Factory Test Procedures. The

Factory Test Procedures may be submitted as a Technical Data

Package.

Factory Test Report

[Four] [_____] copies of the Factory Test Report. The Factory

Test Report may be submitted as a Technical Data Package.

] Existing Conditions Report; G[, [_____]]

[Four] [_____] copies of the Existing Conditions Report.

Start-Up and Start-Up Testing Report; G[, [_____]]

[Four] [_____] copies of the Start-Up and Start-Up Testing

Report. The Start-Up and Testing report may be submitted as a

Technical Data Package.

PVT Phase I Procedures; G[, [_____]]

[Four] [_____] copies of the PVT Phase I Procedures. The PVT

Procedures may be submitted as a Technical Data Package.

PVT Phase I Report; G[, [_____]]

[Four] [_____] copies of the PVT Phase I Report. The PVT Phase

I Report may be submitted as a Technical Data Package.

PVT Phase II Report; G[, [_____]]

[Four] [_____] copies of the PVT Phase II Report. The PVT Phase

II Report may be submitted as a Technical Data Package.

SD-10 Operation and Maintenance Data

SECTION 25 10 10 Page 33

Operation and Maintenance (O&M) Instructions; G[, [_____]]

[Four] [_____] bound O&M Instructions[ and [_____] copies of the

Instructions in PDF format on optical disc]. Index and tab bound

instructions.[ Submit instructions in PDF form as a single PDF

file, or as multiple PDF files with a PDF file table of contents

containing links to the other files.] O&M Instructions may be

submitted as a Technical Data Package.

Preventive Maintenance Work Plan; G[, [_____]]

[Four] [_____] copies of the Preventive Maintenance Work Plan.

The Preventive Maintenance Work Plan may be submitted as a

Technical Data Package.

Basic Training Documentation; G[, [_____]]

Training manuals for Basic Training delivered for each trainee

on the Course Attendance List with [two] [_____] additional copies

delivered for archival at the project site. Submit [two] [_____]

copies of the Course Attendance List with the archival copies.

The Basic Training Documentation may be submitted as a Technical

Data Package.

Advanced Training Documentation; G[, [_____]]

One set of training manuals delivered for each trainee on the

Course Attendance List with [two] [_____] additional copies

delivered for archival at the project site. Submit [two] [_____]

copies of the Course Attendance List with the archival copies.

The Advanced Training Documentation may be submitted as a

Technical Data Package.

Refresher Training Documentation; G[, [_____]]

One set of training manuals delivered for each trainee on the

Course Attendance List with [two] [_____] additional copies

delivered for archival at the project site. Submit [two] [_____]

copies of the Course Attendance List with the archival copies.

The Refresher Training Documentation may be submitted as a

Technical Data Package.

SD-11 Closeout Submittals

Closeout QC Checklist; G[, [_____]]

[Four] [_____] copies of the Closeout QC Checklist.

1.5 PROJECT SEQUENCING

**************************************************************************

NOTE: Table I provides bracketed text in which the

number of days between items may be specified. In

many cases this information will be specified

elsewhere. When project schedule is specified

elsewhere remove bracketed text and Table I will

provide sequencing but not specific intervals. If

time intervals are to be specified here keep the

bracketed text and enter the number of days in the

SECTION 25 10 10 Page 34

space provided.

**************************************************************************

TABLE I: PROJECT SEQUENCING specifies the sequencing of submittals as

specified in paragraph SUBMITTALS (denoted by an 'S' in the 'TYPE' column)

and activities as specified in PART 3 EXECUTION (denoted by an 'E' in the

'TYPE' column).

1.5.1 Sequencing for Submittals

The sequencing specified for submittals is the deadline by which the

submittal must be initially submitted to the Government. Following

submission there will be a Government review period as specified in

Section 01 33 00 SUBMITTAL PROCEDURES. If the submittal is not accepted

by the Government, revise the submittal and resubmit it to the Government

within [14] [_____] days of notification that the submittal has been

rejected. Upon re-submittal there will be an additional Government review

period. If the submittal is not accepted the process repeats until the

submittal is accepted by the Government.

1.5.2 Sequencing for Activities

The sequencing specified for activities indicates the earliest the

activity may begin.

1.5.3 Abbreviations

In TABLE I the abbreviation AAO is used for 'after approval of' and 'ACO'

is used for 'after completion of'.

**************************************************************************

NOTE:

If requiring a Factory Test in PART 3 EXECUTION,

keep "Acceptance of Factory Test Report" in the

DESCRIPTION column for item 1. If NOT requiring a

factory test keep "Notice to proceed" or edit to

indicate other starting condition.

Complete TABLE I by entering the appropriate number

of days in the spaces provided in the SEQUENCING

column.

**************************************************************************

**************************************************************************

NOTE: If this project includes work to be performed

under Section 23 09 00 INSTRUMENTATION AND CONTROL

FOR HVAC, that work will need to be coordinated

with, and in many cases will need to be completed

before, work specified in this Section under

paragraph "Integration of Field Control Systems".

**************************************************************************

**************************************************************************

NOTE: This subpart uses tailoring options:

The Certificate of Networthiness Documentation is

only required for Army projects and is only included

when the ARMY tailoring options is selected.

**************************************************************************

SECTION 25 10 10 Page 35

TABLE I. PROJECT SEQUENCING

ITEM TYPE DESCRIPTION SEQUENCING

(START OF ACTIVITY or

DEADLINE FOR SUBMITTAL)

1 [Acceptance of Factory Test

Report][Notice to proceed][_____]

2 S Existing Conditions Report [_____] days after #1

3 S Design Drawings [_____] days after #1

4 S Product Data Sheets and Certificate

of Networthiness Documentation

[_____] days after #1

5 S UMCS IP Network Bandwidth Usage

Estimate

[_____] days after #1

6 S Pre-construction QC Checklist [_____] days after #1

7 E Install UMCS AAO #2 thru #6

8 E Start-Up and Start-Up Testing ACO #7

9 S Post-Construction QC Checklist [_____] days ACO #8

10 S Computer Software [_____] days ACO #8

11 S Start-Up and Start-Up Testing

Report

[_____] days ACO #8

12 S Draft As-Built Drawings [_____] days ACO #8

13 S PVT Phase I Procedures [_____] days before scheduled start

of #14 and AAO #11

14 E PVT Phase I AAO #13 and #12

15 S PVT Phase I Report [_____] days ACO #14

16 S Preventive Maintenance Work Plan AAO #11

17 S O&M Instructions AAO #11

SECTION 25 10 10 Page 36

TABLE I. PROJECT SEQUENCING

ITEM TYPE DESCRIPTION SEQUENCING

(START OF ACTIVITY or

DEADLINE FOR SUBMITTAL)

18 S Basic Training Documentation AAO #11 and [_____] days before

scheduled start of #19

19 E Basic Training (PVT Phase II) AAO #16, #17 and #18

20 S PVT Phase II Report [_____] days ACO #19

21 S Final As-Built Drawings [_____] days AAO #20

22 S Advanced Training Documentation [_____] days before schedule start

of #23 and AAO #18

23 E Advanced Training ACO #19, [_____] days AAO #22, and

no later than [60] days ACO #19

24 S Refresher Training Documentation [_____] days before #25 and AAO #18

and #22

25 E Refresher Training between [_____] and [_____] days ACO

#19 and AAO #24

26 S Closeout QC Checklist ACO #23

1.6 QUALITY CONTROL (QC) CHECKLISTS

The Contractor's Chief Quality Control (QC) Representative must complete

the QC Checklist in APPENDIX A, and must submit the Pre-Construction QC

Checklist, Post-Construction QC Checklist and Closeout QC Checklist as

specified. The QC Representative must verify each item in the Checklist

and initial in the provided area to indicate that the requirement has been

met. The QC Representative must sign and date the Checklist prior to

submission to the Government.[

The APPENDIX A QC Checklist is available as an editable file at

http://www.wbdg.org/ffc/dod/unified-facilities-guide-specifications-ufgs/ufgs-25-10-10

]

1.7 OPERATION AND MAINTENANCE (O&M) INSTRUCTIONS

Provide UMCS Operation and Maintenance Instructions which include:

a. Procedures for the UMCS system start-up, operation and shut-down.

b. Final As-Built drawings.

c. Routine maintenance checklist, arranged in a columnar format: The

first column listing all installed devices, the second column stating

SECTION 25 10 10 Page 37

the maintenance activity or stating that no maintenance required, the

third column stating the frequency of the maintenance activity, and

the fourth column providing any additional comments or reference.

d. Qualified service organization list including points of contact with

phone numbers.

e. Start-Up and Start-Up Testing Report.

f. Performance Verification Test (PVT) Procedures and Reports.

PART 2 PRODUCTS

2.1 EQUIPMENT REQUIREMENTS

2.1.1 Product Certifications

For computing devices, as defined in FCC Part 15, supplied as part of the

UMCS provide devices which are certified to comply with the requirements

of Class B computing devices.

2.1.2 Product Sourcing

For units of the same type of equipment, provide products of a single

manufacturer. For each major component of equipment provide equipment

with the manufacturer's name and the model and serial number in a

conspicuous place. For materials and equipment, provide new standard

unmodified products of a manufacturer regularly engaged in the

manufacturing of such products.

2.1.3 General Requirements

Provide components that meet the following requirements:

**************************************************************************

NOTE: In particularly hot or cold environments,

increase the temperature range requirements for

equipment in unconditioned space

**************************************************************************

a. Portions of the data communications equipment system installed in

unconditioned spaces must operate properly in an environment with

ambient temperatures between [0 and 49] [_____] degrees C [32 and 120]

[_____] degrees F and ambient relative humidity between 10 percent and

90 percent noncondensing.

b. Components must accept 100 to 125 volts AC (Vac), 60 Hz, single phase,

three wire with a three-pronged, dedicated circuit outlet or be

provided with a transformer to meet the component's power requirements.

c. The equipment must meet the requirements of NFPA 70, UL 60950, NFPA 262,

FCC EMC, and FCC Part 15.

2.1.4 Nameplates

Provide nameplates of laminated plastic identifying the function, network

address, if applicable, and identifier of the device. Laminated plastic

must be at least 3 mm 0.125 inch thick, white with black center core.

Nameplates must be a minimum of 25 by 75 mm 1 by 3 inch with minimum 6 mm

SECTION 25 10 10 Page 38

0.25 inch high engraved block lettering.

2.1.5 Product Data Sheets

**************************************************************************

NOTE: This subpart uses tailoring options: The

sentence containing the PICS requirement is only

included when the BACNET tailoring option is

selected.

**************************************************************************

For all products (equipment) specified in PART 2 and supplied under this

contract, submit copies of all manufacturer catalog cuts and specification

sheets to indicate conformance to product requirements. For Monitoring

and Control (M&C) Software also include the PICS verifying BTL Listing as

a B-AWS.

2.2 CONTROL HARDWARE

2.2.1 Control Protocol Routers

2.2.1.1 LonWorks/IP Router

Provide LonWorks/IP Routers which perform layer 3 routing of CEA-709.1-D

packets over an IP network in accordance with CEA-852-C. The router must

provide the appropriate connection to the IP network and connections to

the CEA-709.3 TP/FT-10 or TP/XF-1250 network. LonWorks/IP Routers must

support the Dynamic Host Configuration Protocol (DHCP; IETF RFC 4361) for

IP configuration and the use of an CEA-852-C Configuration Server (for

CEA-852-C configuration), but must not rely on these services for

configuration. LonWorks/IP Routers must be capable of manual

configuration via a console RS-232 port.

2.2.1.2 BACnet/IP Router

**************************************************************************

NOTE: Include the bracketed text "[, or other

ASHRAE 135]" as needed to allow for integration to

non-MS/TP networks.

**************************************************************************

Provide BACnet/IP Routers which perform layer 3 routing of ASHRAE 135

packets over an IP network in accordance with ASHRAE 135 Annex J and

Clause 6. The router must provide the appropriate connection to the IP

network and connections to a ASHRAE 135 MS/TP[, or other ASHRAE 135]

network. Devices used as BACnet/IP Routers must be BTL Listed and must

support the Network Management-Router Configuration-B (NM-RC-B) BIBB.

2.2.1.3 Modbus/IP Router

Provide Modbus/IP Routers which perform layer 3 routing of MODBUS Protocol/

MODBUS TCP/IP packets over an IP network in accordance with MODBUS Protocol

/MODBUS TCP/IP. The router must provide the appropriate connection to the

IP network and connections to a non-IP MODBUS Protocol/MODBUS TCP/IP

network. Modbus/IP Routers must support the Dynamic Host Configuration

Protocol (DHCP; IETF RFC 4361) for IP configuration but must not rely on

this service for configuration. Modbus/IP Routers must be capable of

disabling the capability for remote configuration of Modbus routing

information from the IP network.

SECTION 25 10 10 Page 39

2.2.2 Monitoring and Control (M&C) Controller Hardware

**************************************************************************

NOTE: This subpart uses tailoring options: "a

Niagara Framework Supervisory Gateway" is only

included when the NIAGARA FRAMEWORK tailoring option

is selected.

**************************************************************************

Provide Monitoring and Control (M&C) Controller Hardware which is a

Niagara Framework Supervisory Gateway or a microprocessor-based direct

digital control hardware and which communicates over the UMCS IP network

using one of:

a. CEA-709.1-D in accordance with CEA-852-C and using only Standard

Network Variable Types (SNVTs) as defined by the LonMark SNVT List.

b. ASHRAE 135 in accordance with ASHRAE 135 Annex J and using only

Standard ASHRAE 135 services.

Monitoring and Control (M&C) Controller Hardware must either meet the

requirements of the LonMark Interoperability Guide or be BTL Listed.

2.2.3 BACnet Supervisory Controller Hardware

**************************************************************************

NOTE: This subpart only applies to BACnet systems

and is only included when the BACNET tailoring

option is only included when the BACNET tailoring

option is selected.

**************************************************************************

Provide BACnet Supervisory Controller Hardware which is direct digital

control hardware and which:

a. is BTL Listed

b. communicates using ASHRAE 135 over an IP network in accordance with

ASHRAE 135 Annex J

c. has a configurable Object_Name Property

d. supports the following BIBBS

(1) DS-RP-B (Data Sharing–Read Property–B) BIBB for Objects requiring

read access from the M&C Software

(2) DS-WP-B (Data Sharing–Write Property–B) BIBB for Objects requiring

write access from the M&C Software.

(3) SCHED-E-B (Scheduling-External-B)

(4) AE-N-I-B (Alarm and Event-Notification Internal-B)

(5) AE-ACK-B (Alarm and Event-ACK-B)

(6) T-VMT-I-B (Trending-Viewing and Modifying Trends-Internal-B)

SECTION 25 10 10 Page 40

(7) T-ATR-B (Trending-Automated Trend Retrieval-B)

e. has a Writable Recipient_List Property of the Notification Class Object

2.2.4 Control Protocol Gateways

**************************************************************************

NOTE: FYI: Except for the use of Niagara Framework

Supervisory Gateways with Niagara Framework M&C

Software, Gateways should be used only for the

integration of legacy building control systems

(HVAC, lighting etc) or for the integration of new

or legacy utility control systems. Gateways should

not be used to permit the installation of new

building control systems which do not use,CEA-709.1-D

or ASHRAE 135.

Indicate if additional capability may be required.

Note that since the Legacy system should not change

this requirement shouldn't be needed, and when used

will normally be intended to cover the case of

'forgotten' points (when the mapping requirements

from the legacy system have not been fully/properly

identified). Requiring excess capacity may add cost.

**************************************************************************

**************************************************************************

NOTE: This subpart uses tailoring options. Fox

Protocol is included in the protocol list only when

the NIAGARA FRAMEWORK tailoring option is selected.

**************************************************************************

Provide Control Protocol Gateways which perform bi-directional protocol

translation between two of the following protocols, or between one of the

following protocols and another protocol: CEA-709.1-D, ASHRAE 135,

MODBUS Protocol, MODBUS TCP/IP, Fox protocol, and OPC DA. Provide Control

Protocol Gateways which also meet the following requirements.

a. Gateways must have two or more separate network connections, each

appropriate for the protocol and media used. A single network

connection must not be used for both protocols.

b. Gateways must be capable of being installed, configured and programmed

through the use of instructions in the manual supplied by the

Contractor.

c. Provide and license to the Government all software required for

gateway configuration.

d. Gateways must retain their configuration after a power loss of an

indefinite time, and must automatically return to their pre-power loss

state once power is restored.

e. Gateways must provide capacity for mapping all required points as

indicated[ plus an additional [10 percent][_____]] between the two

protocols it uses.

f. Gateways must, in addition, meet all requirements specified (in the

following subparagraphs) for each of the two protocols it translates.

SECTION 25 10 10 Page 41

2.2.4.1 Gateway for CEA-709.1

For a gateways using CEA-709.1-D provide gateways which meet the following

requirements in addition to the requirements for all gateways:

a. It must allow bi-directional mapping of data in the Gateway to

Standard Network Variable Types (SNVTs) according to the

LonMark SNVT List.

b. Gateways communicating CEA-709.1-D over an IP network must communicate

in accordance with CEA-852-C.

c. It must allow of its standard network variables (SNVTs) and support

transmitting data using the "min, max, and delta" (throttling and

heartbeat) methodology.

d. It must provide the ability to label SNVTs.

e. It must supply a LonMark external interface file (XIF) as defined in

the LonMark XIF Guide for use with LNS tools and utilities.

f. It must have a "service pin" which, when pressed, will cause the

Gateway to broadcast its 48-bit NodeID and ProgramID over the network.

g. It must provide a configurable self-documenting string.

2.2.4.2 Gateway for ASHRAE 135

For gateways using ASHRAE 135 provide gateways which meets the following

requirements in addition to the requirements for all gateways:

a. It must allow bi-directional mapping of data in the Gateway to

Standard Objects as defined in ASHRAE 135.

b. All ASHRAE 135 Objects must have a configurable Object_Name Property.

c. It must be BTL Listed.

d. Gateways communicating ASHRAE 135 over an IP network must communicate

in accordance with ASHRAE 135 Annex J.

**************************************************************************

NOTE: The following 2 requirements cover 2 ways in

which the gateway can be used:

1) The gateway communicates with a BACnet building

control system. In this case the gateway has to be

able to read from and write to devices in the BACnet

building control system.

2) The gateway communicates with a BACnet front-end

(M&C Software). In this case the gateway must be

able to be read from and be written to by the M&C

Software. In addition, the gateway must provide

scheduling, alarming and trending for the building

system.

Note that it would be possible to have a

SECTION 25 10 10 Page 42

BACnet-BACnet gateway that is used in both of these

ways at the same time.

**************************************************************************

e. Gateways communicating ASHRAE 135 to a field control systems must

support the DS-RP-A (Data Sharing–Read Property–A) BIBB and the

DS-WP-A (Data Sharing–Write Property–A) BIBB.

f. Gateways communicating ASHRAE 135 to the M&C Software or to a BACnet

Supervisory Controller must support the DS-RP-B (Data Sharing–Read

Property–B) BIBB for Objects requiring read access from the M&C

Software and the DS-WP-B (Data Sharing–Write Property–B) BIBB for

Objects requiring write access from the M&C Software

2.2.4.3 Gateway for Modbus

**************************************************************************

NOTE: This subpart uses tailoring options.

Requirements for the presentation of data in

accordance with the MODBUS REQUIREMENTS paragraph is

only included when the MODBUS tailoring option is

selected.

**************************************************************************

For gateways that use MODBUS Protocol/MODBUS TCP/IP provide gateways that

meet the requirements specified for all gateways and which allow

bi-directional mapping of data in the Gateway to MODBUS Protocol/

MODBUS TCP/IP registers using the four standard Modbus register types

(Discrete Input, Coil, Input Register,and Holding Register). Gateways

communicating MODBUS Protocol/MODBUS TCP/IP to the M&C Software must

communicate via MODBUS Protocol/MODBUS TCP/IP over TCP/IP and must present

floating point values, character values, and date values using the

appropriate data type as specified in paragraph MODBUS REQUIREMENTS.

2.2.4.4 Gateway for OPC

For gateways that use OPC DA, provide gateways that meet the requirements

specified for all gateways and which allow bi-directional mapping of data

in the Gateway using OPC DA tags and which communicate over an IP network

in accordance with OPC DA.

2.2.4.5 Gateway for DNP3

For gateways that use DNP3, provide gateways that meet the requirements

specified for all gateways and which allow bi-directional mapping of data

in the Gateway to DNP3 object groups and variations as defined by IEEE 1815.

Gateways communicating DNP3 over an IP network must communicate in

accordance with the LAN/WAN Networking volume of IEEE 1815.

2.2.4.6 Niagara Framework Supervisory Gateway

**************************************************************************

NOTE: This subpart is only required for Niagara

Framework systems, or for Navy Projects and is only

included when the NIAGARA FRAMEWORK or NAVY

tailoring option is selected.

**************************************************************************

**************************************************************************

SECTION 25 10 10 Page 43

NOTE: FYI - The Niagara Framework Supervisory

Gateway is known by many names within industry, and

this specification uses the name "Niagara Framework

Supervisory Gateway" in order to remain vendor

neutral. Probably the most common term used for

this device in industry is a "Java Application

Control Engine", or JACE.

**************************************************************************

Niagara Framework Supervisory Gateway Hardware must:

a. be direct digital control hardware.

b. have an unrestricted interoperability license and a Niagara

Compatibility Statement (NiCS) that follows the Tridium Open NiCS

Specification.

c. manage communications between a field control network and the Niagara

Framework Monitoring and Control Software and between itself and other

Niagara Framework Supervisory Gateways. Niagara Framework Supervisory

Gateway Hardware must use Fox protocol for communication with other

Niagara Framework Components.

d. be fully programmable using the Niagara Framework Engineering Tool and

support the following:

(1) Time synchronization, Calendar, and Scheduling using Niagara

Scheduling Objects

(2) Alarm generation and routing using the Niagara Alarm Service

(3) Trending using the Niagara History Service and Niagara Trend Log

Objects

(4) Integration of field control networks using the Niagara Framework

Engineering Tool

(5) Configuration of integrated field control system using the Niagara

Framework Engineering Tool when supported by the field control

system

e. meet the following minimum hardware requirements:

(1) [One][Two] 10/100/1000 Mbps Ethernet Ports

(2) One port compatible with the field control system to be integrated

using this product.[

(3) Central Processing Unit of 600 Mhz or higher.][

(4) Embedded operating system.]

f. provide access to field control network data and supervisory functions

via web interface and support a minimum of 16 simultaneous users

2.4.6 CEA-852-C Configuration Server

**************************************************************************

NOTE: This subpart only applies to LonWorks systems

and is only included when the LONWORKS tailoring

option is selected.

**************************************************************************

Provide CEA-852-C configuration server software meeting the requirements

of CEA-852-C.

2.4.7 CEA-709.1-D Network Configuration Tool

**************************************************************************

NOTE: This subpart only applies to LonWorks systems

and is only included when the LONWORKS tailoring

option is selected..

SECTION 25 10 10 Page 50

**************************************************************************

Provide a network configuration tool software which:

a. Solely uses LonWorks Network Services (LNS) for all network

configuration and management of CEA-709.1-D devices.

b. Is capable of executing LNS plug-ins.

c. Is capable of performing network database reconstruction of an

CEA-709.1-D control network, such that if connected to an existing

CEA-709.1-D network it has the ability to query the network and create

an LNS database for that network.

d. Allows configuration of the network while off-line such that an

operator may set up changes to the network while disconnected from the

network, and then execute all of them once connected.

e. Includes the standard LNS Report Generator and is capable of

generating and printing the following reports:

(1) A table containing domain/subnet/node address and node identifier

for the entire network or any subset thereof, selected by the user.

(2) A table containing Standard Network Variable (SNVT) input and

output details for any CEA-709.1-D device on the network.

(3) A table containing Standard and User-Defined Configuration

Properties (SCPTs and UCPTs) for any CEA-709.1-D device on the

network.

f. Is capable of merging two existing standard LNS databases into a

single standard LNS database.

2.4.8 BACnet Network Browser

**************************************************************************

NOTE: This subpart only applies to BACnet systems

and is only included when the BACNET tailoring

option is selected.

**************************************************************************

Provide a BACnet Network Browser software that:

a. Can perform full discovery of a ASHRAE 135 system including but not

limited to discovery of all ASHRAE 135 devices, the ASHRAE 135 Objects

and Properties of each device, and the standard ASHRAE 135 services

supported by each device.

b. Can read any ASHRAE 135 Property of any Object in any device.

Proprietary Properties may be presented as read without further

interpretation.

c. Can write any Standard ASHRAE 135 Property of any Object in any device.

d. Supports segmentation.

e. Supports all of the following BIBBs:

SECTION 25 10 10 Page 51

(1) DM-ANM-A (Device Management-Automatic Network Management-A)

(2) DM-ADM-A (Device Management-Automatic Device Management-A)

(3) DM-DDB-A (Device Management-Dynamic Device Binding-A)

(4) DM-DOB-A (Device Management-Dynamic Object Binding-A)

(5) DS-RP-A (Data Sharing-Read Property-A)

(6) DS-RPM-A (Data Sharing-Read Property Multiple-A)

(7) DS-WP-A (Data Sharing-Write Property-A)

2.4.9 Niagara Framework Engineering Tool

**************************************************************************

NOTE: This subpart only applies to Niagara

Framework systems and is only included when the

NIAGARA FRAMEWORK tailoring option is selected.

**************************************************************************

Provide Niagara Workbench or an equivalent Niagara Framework engineering

tool software which:

a. has unrestricted interoperability license and a Niagara Compatibility

Statement (NiCS) which follows the Tridium Open NiCS Specification.

b. is capable of performing network configuration for Niagara Framework

Supervisory Gateways and Niagara Framework Monitoring and Control

Software.

c. is capable of programming and configuring Niagara Framework

Supervisory Gateways and Niagara Framework Monitoring and Control

Software.

d. is capable of discovery of Niagara Framework Supervisory Gateways and

all points mapped into each Niagara Framework Supervisory Gateway and

making these points accessible to Niagara Framework Monitoring and

Control Software.

2.4.10 Monitoring and Control (M&C) Software

**************************************************************************

NOTE: Designer should choose the minimum number of

points and clients the M&C software is required to

accommodate based on the project site's master

plan. The initial number of points to be

accommodated should be chosen such that it is

sufficient to cover all current and known future

projects. The total system expansion requirement

should be based on potential/anticipated future

projects.

It's a good idea to obtain pricing for several

price-points between the current specified

points/clients and the future number of

points/clients. Depending on the vendor the cost

increase for system expansion may be drastically

SECTION 25 10 10 Page 52

different.

For non-Niagara Framework systems, points means

"points that the M&C software can read/write on the

network". In general, points will be SNVTs for

LonWorks and the Present Value Property of Objects

for BACnet. Other examples of Points are other

BACnet Properties or LonWorks configuration

properties/configuration network variables. For

Modbus, a point will generally be a Modbus register.

For OPC, a point will be an OPC "tag".

For the Niagara Framework, point licensing only

applies to points directly integrated to the Web

Supervisor without first being brought into a

Niagara Framework Supervisory Gateway. Discuss with

the installation whether integration will generally

be accomplished via Niagara Framework Supervisory

Gateways (this is the normal method) or not before

determining a point licensing requirement When

integration will "always" be through a Niagara

Framework Supervisory Gateway change the number of

network points required below to zero or a very

small number. When requiring network points

indicate in the space provided the protocol drivers

required and network points required to be licensed

by each.

This UFGS requires the use of Web based clients

(previous versions of this UFGS did not, but most

vendors support web-browser based clients and this

no longer overly restricts competition.)

FYI: The following paragraphs/pages (the M&C

software requirements) specify functionality that is

required for the M&C Software but that may not be

achievable due to lack of data/support at the

building level. In order to meet future needs these

requirements should be kept. It is expected that

they are usually part of the 'standard' capabilities

of this type of software.

**************************************************************************

**************************************************************************

NOTE: This subpart uses tailoring options to

indicate requirements for the M&C software in the

first paragraph. Only requirements related to

selected tailoring options are included.

**************************************************************************

Provide monitoring and control (M&C) software which is a client-server

software package with a graphical user interface (GUI) using web-browser

based clients. Provide Niagara Framework Web Supervisor or equivalent

Niagara Framework monitoring and control software which communicates with

Niagara Framework field control systems using the Fox protocol. Provide

M&C Software which communicates via CEA-709.1-D, and ASHRAE 135, and

MODBUS Protocol/MODBUS TCP/IP, and OPC DA. The M&C Software may support

other field control protocols. Provide M&C Software which is BACnet

Testing Laboratories Certified ("Listed") as a B-AWS.

SECTION 25 10 10 Page 53

Provide a single software package which implements the Scheduling,

Alarming, Trending, Graphical System Display, and System Display Editor

functionality. Other specified M&C functionality may be implemented in

the same software package or in additional software packages. As

specified in PART 3 EXECUTION, the M&C Software must operate on Server

hardware, except that software for Point Calculations and Demand Limiting

may operate on M&C Controller Hardware.

2.4.10.1 M&C Software License

License the M&C Software as specified. Use of multiple copies of M&C

Server software working in coordination and sharing data between them such

that they function as, and appear to an operator as, a single M&C Server

is permitted to meet these requirements.

2.4.10.1.1 Network Points

**************************************************************************

NOTE: This subpart uses tailoring options:

1) The sentence referring to Niagara Framework

systems is included only when the NIAGARA FRAMEWORK

tailoring option is selected.

2) The sentence referring to Web Supervisor M&C

Software is only included when the NIAGARA FRAMEWORK

tailoring option is selected.

**************************************************************************

For Niagara Framework systems, a network point is a point brought directly

into the Web Supervisor M&C Software through a protocol other than the Fox

Protocol and via a Niagara Framework Supervisory Gateway. Provide M&C

Software and licensing to support no less than than [_____] network

points, and to be capable of expansion to support no less than [50,000]

[_____] network points. [Provide Web Supervisor M&C Software which

includes the following drivers, each of whish is licensed for a number of

network points as follows: [____].]

2.4.10.1.2 Web Clients

Provide M&C Software and licensing to support no less than [10] [____]

simultaneous web clients with no limit on the total number of web

clients. M&C Software must be capable of expansion to support no less

than [30] [_____] simultaneous web clients.

2.4.10.1.3 Calculations

Provide M&C Software and licensing to support no less than one calculated

point for every ten network points (see "Network Points" above).

2.4.10.1.4 Other Points

For installations using M&C Software installed on M&C Controller Hardware

(as opposed to Server hardware), provide additional licensing to support

additional network points for the communications between portions of the

M&C Software installed on different hardware. For example, if the

Calculations requirement is performed by M&C Software installed on

Controller hardware, the M&C Software must be licensed for additional

network points to cover the network points required for communication

SECTION 25 10 10 Page 54

between the Controller hardware and the Server hardware.

2.4.10.1.5 Alarming

**************************************************************************

NOTE: This subpart uses tailoring options:

1) the phrase "alarm generation and" and the work

"points" is included if the LONWORKS, MODBUS or OPC

tailoring option is selected.

2) the phrase "ASHRAE 135 Alarm Event Notifications"

is included if the BACNET tailoring option is

selected.

**************************************************************************

Provide M&C Software and licensing to support alarm generation and the

handling (routing) of alarms for no less than [10,000] [_____] points and

ASHRAE 135 Alarm Event Notifications.

2.4.10.1.6 Trending

Provide M&C Software and licensing to support a minimum of [8,000] [_____]

simultaneous trends.

[2.4.10.1.7 Scheduling

**************************************************************************

NOTE: This subpart only applies to LonWorks,

Modbus, or OPC systems and is only included when the

LONWORKS, MODBUS or OPC tailoring option is selected.

**************************************************************************

**************************************************************************

NOTE: When LonWorks tailoring is selected, this

paragraph appears in brackets. This is due to

changes in the requirements for LonWorks field

control systems. Until recently LonWorks did not

support an open means of configuring schedules in

field control systems, so all scheduling was done at

the M&C Software. The Simple Schedule Functional

Profile now provides a standard means for schedule

configuration in the field control systems, and is a

requirement in Section 23 09 23.01 LONWORKS DIRECT

DIGITAL CONTROL FOR HVAC AND OTHER BUILDING CONTROL

SYSTEMS.

Keep the bracketed text for Modbus or OPC, or to

maintain compatibility with LonWorks systems which

do not employ the Simple Scheduler and thus require

scheduling at the M&C Software. If Modbus and OPC

are not required and all LonWorks field control

systems will use the Simple Scheduler, the bracketed

text can be removed.

When uncertain, keep the bracketed text as most M&C

Software can support this requirement and keeping

the ability to perform scheduling at the M&C

Software will support a wider range of field control

systems.

SECTION 25 10 10 Page 55

**************************************************************************

Provide M&C Software and licensing to support a minimum of [200] [_____]

user-definable schedules.

]2.4.10.1.8 Niagara Framework Open License

**************************************************************************

NOTE: This subpart only applies to Niagara

Framework systems and is only included when the

NIAGARA FRAMEWORK tailoring option is selected.

**************************************************************************

Provide M&C Software with an unrestricted interoperability license and a

Niagara Compatibility Statement (NiCS) which follows the Tridium Open NiCS

Specification.

2.4.10.2 M&C Software Update Licensing

**************************************************************************

NOTE: The installation may procure its own software

update licensing or contract and thus need less than

5 years. Alternatively the installation may require

longer than five years (although this will likely

increase the costs significantly). Coordinate with

the installation to determine if they have any

specific requirement; if they don't then keep the 5

year requirement.

**************************************************************************

In addition to all other licensing requirements, provide M&C Software

licensing which includes licensing of the following software updates for a

period [of no less than 5 years][____]:

a. Security and bug-fix patches issued by the M&C Software manufacturer.

b. Security patches to address any vulnerability identified in the

National Vulnerability Database at http://nvd.nist.gov with a Common

Vulnerability Scoring System (CVSS) severity rating of MEDIUM or

higher.

2.4.10.3 Supported Field Control Protocols

**************************************************************************

NOTE: FYI: one of the integration methods for

legacy systems is to use a protocol driver (a

'software gateway') in the M&C software to integrate

the legacy system, and these requirements permit the

M&C Software to support protocols other than those

specifically required in this specification.

**************************************************************************

**************************************************************************

NOTE: WARNING - The BACnet tailoring option has

been selected with another protocol tailoring option

(LonWorks, Modbus, OPC). As described in UFC

3-470-01, many of the Monitoring and Control

Software packages which support BACnet support ONLY

BACnet, so the inclusion of other protocol tailoring

SECTION 25 10 10 Page 56

options may unnecessarily limit the number of

vendors able to provide the UMCS. The need for

supporting multiple protocols at the Monitoring and

Control Software should be verified/checked with the

project site. Note that any protocol can be

integrated to the UMCS with the use of a gateway, so

omitting a tailoring option does not prohibit the

integration of systems using that protocol.

See UFC 3-470-01 for more information.

**************************************************************************

**************************************************************************

NOTE: WARNING - The Niagara Framework tailoring

option has been selected with the LonWorks tailoring

option. As described in UFC 3-470-01, LNS-based

LonWorks (required by the LonWorks tailoring option)

is generally not compatible with the Niagara

Framework.

See UFC 3-470-01 for more information.

**************************************************************************

Provide M&C Software which supports field control protocols as follows:

**************************************************************************

NOTE: Due to the use of tailoring options in the

following list of requirements not all requirements

will be included in all projects and items may

require renumbering.

**************************************************************************

**************************************************************************

NOTE: The following list paragraph is included only

when the LONWORKS tailoring option is selected.

**************************************************************************

a. The M&C Software must include a driver to LNS, or a driver to an OPC

interface to LNS, or a driver to CEA-852-C, and must be capable of

reading and writing any SNVT on the CEA-852-C network. Software with

a driver to LNS or a driver to an OPC interface to LNS must

communicate with field control systems via LNS using this driver.

Software with a driver to CEA-852-C must obtain all communication

information (such as device addresses and network variable indices)

from LNS and must automatically update this information whenever the

LNS Database changes.

**************************************************************************

NOTE: The following list paragraph is included only

when the BACNET tailoring option is selected.

**************************************************************************

b. The M&C Software must include a driver to ASHRAE 135 over IP in

accordance with ASHRAE 135 Annex J.

**************************************************************************

NOTE: The following list paragraph is included only

when the MODBUS tailoring option is selected.

**************************************************************************

SECTION 25 10 10 Page 57

c. The M&C Software must include a driver to MODBUS Protocol/MODBUS TCP/IP

over TCP/IP. The M&C Software must be capable of reading and writing

the Modbus data types as defined in paragraph MODBUS REQUIREMENTS and

must, in addition, be capable of manipulating and presenting arbitrary

data formats derived from the four standard Modbus data types.

**************************************************************************

NOTE: The following list paragraph is included only

when the OPC tailoring option is selected.

**************************************************************************

d. The M&C Software must be an OPC DA client.

**************************************************************************

NOTE: The following list paragraph is included only

when the NIAGARA FRAMEWORK tailoring option is

selected.

**************************************************************************

e. The Software must use the Niagara Framework and must communicate with

Niagara Framework Supervisory Gateways using the Fox protocol.

f. The M&C Software may, in addition, include drivers to other protocols.

Provide M&C Software capable of reading values from and writing values to

points via any supported field protocol, and capable of reading values

from one field protocol and writing them to another. All points obtained

from any field protocol must be available to all M&C Software

functionality.

2.4.10.4 Supported Enterprise Protocols

Provide M&C Software which supports oBIX, BACnet Web Services or OPC as an

enterprise protocol and which meets the following requirements:

a. It is able to read values from any point or collection of points

(network point, internal point, trend log or schedule) and transmit

these values via the enterprise protocol.

b. It is able to receive data via the enterprise protocol and use this

data to change the value of any point.

c. License the enterprise protocol interface to the project site and

document he interface such that any system capable of communicating

with that protocol can be used to read and write data from the M&C

Software.

2.4.10.5 Point Information

Every point, both network and internal, in the M&C Software must contain

the following fields:

2.4.10.5.1 Name

A configurable name used for identification of the point within the M&C

Software.

SECTION 25 10 10 Page 58

2.4.10.5.2 Description

A configurable description of no less than 80 alpha-numeric characters.

2.4.10.5.3 Value

A field containing the current point value.

2.4.10.5.4 Units

A field containing the engineering units.

2.4.10.5.5 Source

A field identifying the source of the point. For network points, this is

generally the address or identification of the field device (for example,

the Domain-Subnet-Node address for LonWorks field control devices or the

DeviceID for BACnet devices).

2.4.10.6 Point Calculations

Provide M&C software capable of performing calculations and computing the

value of a calculated point based on the values of two or more network

points and calculated points. Mathematical operators must include:

addition, subtraction, multiplication, division, exponentiation (y^x,

power), square root, reciprocal, natural logarithm, sin, cos, tan, arcsin,

arccos, arctan, and parenthesis. Pi and e must be available as constants

for use in calculations.

2.4.10.7 Browser-Based Graphical User Interface (GUI)

**************************************************************************

NOTE: The contractor will require a certificate for

the M&C Web Server (in order to use HTTPS as

required here). Coordinate with the project site IT

organization (NEC) to obtain this certificate.

**************************************************************************

Provide M&C Software which includes a web-browser based (client-server)

graphical user interface through which all M&C Software functionality,

except for the Graphics Editor, System Display Editor, report

configuration, point calculation configuration, and enterprise protocol

configuration, is accessible.

Provide graphical user interface web server and web clients meeting the

following requirements:

a. The web server must use HTTPS based on the Transport Layer Security

(TLS) Protocol in accordance with IETF RFC 7465 using a

Government-furnished certificate.

b. The graphical user interface must be Common Access Card (CAC) enabled:

It must support web client authentication using certificates obtained

from a Department of Defense Common Access Card (CAC) Smart Card.

c. The web client must operate on any version of Windows currently

supported by Microsoft.

d. The web client must function in the most recent three version of

SECTION 25 10 10 Page 59

Internet Explorer [and [the most recent three versions of

Firefox][____]].

e. The web client must not require a connection to any server other than

the M&C Server.

f. The web client must function in a browser with Java, Shockwave,

Silverlight, and Flash installed. The client may require a download

of mobile code from the M&C Server, but must not require the download

of additional browser plug-ins or add-ins and there must be no limit

on the number of downloads. The client must not require ActiveX.

2.4.10.8 Passwords

**************************************************************************

NOTE: Designer must choose if password management

for M&C software is performed

a) by the OS

or

b) by the M&C software itself

or

c) if the decision is left to the Contractor.

The password requirements here provide a simple

basis for user authentication. More complex

password schemes may be required by the

installation. Coordinate with the installation and

if they have more detailed or complex password

requirements enter them in the space provided.

Otherwise keep the bracketed defaults.

**************************************************************************

Provide M&C software with user-based access control to M&C functionality.

The M&C Software must recognize at least [100] [_____] separate users and

have [at least 4] [____] levels of user permissions. User permission

levels (from most restrictive to most permissive) must include:[

a. Permission Level 1: View-only access to the graphical user interface.

b. Permission Level 2: Permission Level 1 plus acknowledge alarms and set

up (configure) trends and reports.

c. Permission Level 3: Permission Level 2 plus override points and set up

(configure) alarms, schedules and demand limiting.

d. Permission Level 4: Permission Level 3 plus create and modify

Graphical System Displays using the System Display Editor.][____]

Passwords must not be displayed and must not be logged. The system must

maintain a disk file on the server hardware logging all activity of the

system. This file must maintain, as a minimum, a record of all

operators logged onto the system, alarm acknowledgments, commands issued

and all database modifications. If the file format is not plain ASCII

text, provide a means to export or convert the file to plain ASCII text.

Provide a mechanism for archiving the log files for long term record

storage.

SECTION 25 10 10 Page 60

2.4.10.9 Graphical System Displays

Provide graphical displays consisting of building system (air handler

units, VAV boxes, chillers, cooling towers, boilers, etc.) graphic

displays. Data associated with an active display must be updated at least

once every 5 seconds.

2.4.10.9.1 Navigation Scheme

System graphic displays of building systems and points must be

hierarchical displays using a building-to-equipment point-and-click

navigation scheme which allows navigation from a garrison-wide display,

through a building-wide display to the individual units. Each display must

show the building name and number. Each display must show system wide

data such as outside air temperature and humidity in the case of an HVAC

system application.

a. For each Building or Building Sub-Area display, show the building foot

print and basic floor plan, and clearly show and distinguish between

the individual zones and the equipment serving each zone and space.

Show all space sensor and status readings, as applicable, for the

individual zones such as space temperature, humidity, occupancy

status, etc. Show the locations of individual pieces of monitored and

controlled equipment.

**************************************************************************

NOTE: Coordinate with the project site and select

the style of representation for equipment.

When making this selection consider the effect that

detailed graphics have on the performance of the

user interface; the more complex the graphic, the

longer it will take for the page to load.

**************************************************************************

b. For each equipment display show a [one-line diagram control

schematic][3-dimensional] representation of the individual pieces of

equipment using the symbols and M&C point data types as specified.

Use different colors and textures to indicate various components and

real time data. Use consistent color and texture meanings across all

displays.

c. Provide displays which clearly distinguish between the following point

data types and information:

(1) Real-time data.

(2) Other user-entered data.

(3) Devices in alarm (unacknowledged).

(4) Out-of-range, bad, or missing data.

(5) Points which are overridden.

2.4.10.9.2 Navigation Commands

Provide system displays which support English language operator commands

via point-and-click mouse or keyboard entry for defining and selecting

SECTION 25 10 10 Page 61

points, parameters, graphics, report generation, and all other functions

associated with operation. The operator commands must be usable from any

operator workstation with individual operator passwords as specified.

2.4.10.10 Graphic Editor

Provide a fully featured graphics editor and capable of creating custom

graphics and graphic symbols for use by the System Display Editor.

2.4.10.11 System Display Editor

Provide a system display editor which allows the user to create, modify,

and delete graphic displays. The display editor may have a separate user

interface and is not required to be accessible via the web browser

interface. Provide a display editor which includes the following

functions:

a. Create and save displays. Save an existing or modified display as a

new display (i.e. "save as")

b. Group and ungroup graphics, where graphics include both alphanumeric

and graphic symbols, and where a grouped graphic is manipulated as a

single graphic.

c. Place, locate, resize, move, remove, reposition, rotate and mirror a

graphic on a display.

d. Overlay graphics over other graphics and assign depths such that when

there are coincident graphics the one on top is visible.

e. Modify graphic properties based on the value of network points and

create conditions governing the display of a graphics such that

different graphics are visible based on the value of network points or

calculated points

f. Integrate real-time data with the display.

g. Establish connecting lines.

h. Establish sources of latest data and location of readouts.

i. Display analog values as specified.

j. Assign conditions which automatically initiate a system display.

k. Include library of display symbols which include: Pump, Motor, Two and

Three-way Valves, Flow Sensing Element, Point and Averaging

Temperature Sensors, Pressure Sensor, Humidity Sensor, Single and

Double Deck Air Handling Unit, Fan, Chiller, Boiler, Air Compressor,

Chilled Water Piping, Steam Piping, Hot Water Piping, Ductwork, Unit

Heater, Pressure Reducing Valve, Damper, Electric Meter, Limit Switch,

Flow Switch, High- and Low- Point and Averaging Temperature Switches,

High- and Low- Pressure Switches, Coil, Solenoid Valve, Filter,

Condensing Unit, Cooling Tower, Variable Frequency Drive (VFD), Heat

Exchanger, Current Sensing Relays, Generator, Circuit Breaker,

Transformer, Tank. Symbols must at a minimum conform to ASHRAE FUN SI

ASHRAE FUN IP where applicable.

SECTION 25 10 10 Page 62

2.4.10.12 Scheduling

**************************************************************************

NOTE: FYI: For BACnet systems it is expected that

there will be Scheduling Objects in the field

control system and the M&C Software will edit

(configure) these schedules.

For LonWorks the M&C software will be the primary

method of scheduling; building systems have 'backup'

scheduling capability in the event of a loss of

communication with the M&C Software Server.

For Niagara Framework systems it is expected that

there will be Niagara Framework Scheduling Objects

in the Niagara Framework Supervisory Gateway(s) and

the M&C Software will edit (configure) these

schedules.

In general it is expected that Modbus and OPC will

be used for the integration of utility control

systems which will likely have their own scheduling

capability. In this case scheduling from the M&C

Software will be for secondary/supervisory functions.

Due to the use of tailoring options in the following

list of requirements not all requirements will be

included in all projects and items may require

renumbering.

**************************************************************************

**************************************************************************

NOTE: The following TWO list paragraph is included

only when the LONWORKS, MODBUS or OPC tailoring

option is selected.

**************************************************************************

a. Provide M&C software capable of changing the value of any network

point according to a schedule. The M&C Software must be capable of

scheduling points to any value, including a "null" or invalid value if

one is defined for the data type of the point.

b. The specified scheduling functions must be operator accessible and

adjustable via the graphical user interface. Each schedule must be

able to change the value of multiple points. The M&C software must

reinforce all schedules by transmitting the scheduled value no less

than once every 30 minutes.

**************************************************************************

NOTE: The following list paragraph is included only

when the BACNET tailoring option is selected.

**************************************************************************

c. The M&C software must be capable of performing time synchronization

and configuring Schedule Objects in ASHRAE 135 field devices in

accordance with the DM-MTS-A (Device Management-Manual Time

SECTION 25 10 10 Page 63

Synchronization-A).

**************************************************************************

NOTE: The following list paragraph is included only

when the NIAGARA FRAMEWORK tailoring option is

selected.

**************************************************************************

d. The M&C software must be capable of performing time synchronization

and configuring Niagara Framework Schedule Objects in Niagara

Framework Supervisory Gateways.

e. The M&C Software must include a scheduling graphic display, accessible

via the graphical user interface, with the following fields and

functions:

(1) Current date and time.

(2) System identifier(s) and name(s), including location information

such as Building name(s) and number(s).

(3) System group. Systems grouped by the user to perform according to

a common schedule.

(4) Weekly schedules. For each system, a weekly schedule based on a

seven day per week schedule with independent schedules for each

day of the week including no less than 6 value changes per day.

(5) Holiday and special event schedules. Support for holiday and

special event calendar schedules independent of the daily

schedule. Special event schedules include one-time events and

recurring events. Scheduling of one-time events include the

beginning and ending dates and times of the event. Holiday and

special event schedules must have precedence over device weekly

schedules.

2.4.10.13 Alarms

Provide M&C Software meeting the following minimum requirements for alarms:

**************************************************************************

NOTE: The following list paragraph uses tailoring

options:

1) "generating alarms by comparing the value of any

point from any connected system to user-configurable

limits" is included when the LONWORKS, MODBUS or OPC

tailoring option is selected

2) "configuring alarms in ASHRAE 135 field devices

in accordance with the B-AWS BIBBs" is included when

the BACNET tailoring option is selected.

3) "configuring alarms in Niagara Framework

Supervisory Gateways using the Niagara Alarm

Service" is included when the NIAGARA FRAMEWORK

tailoring option is selected.

**************************************************************************

SECTION 25 10 10 Page 64

a. The M&C software must be capable of generating alarms by comparing the

value of any point from any connected system to user-configurable

limits, and configuring alarms in ASHRAE 135 field devices in

accordance with the B-AWS BIBBs, and configuring alarms in Niagara

Framework Supervisory Gateways using the Niagara Alarm Service.

**************************************************************************

NOTE: The following list paragraph uses tailoring

options:

1) "alarms generated by the M&C Software" is

included when the LONWORKS, MODBUS or OPC tailoring

option is selected

2) "alarms received as an ASHRAE 135 Alarm Event

Notifications" is included when the BACNET tailoring

option is selected.

3) "alarms received from a Niagara Framework

Supervisory Gateway" is included when the NIAGARA

FRAMEWORK tailoring option is selected.

**************************************************************************

b. The M&C software must be capable of handling (routing) alarms

generated by the M&C Software, and alarms received as an ASHRAE 135

Alarm Event Notifications, and alarms received from a Niagara

Framework Supervisory Gateway.

**************************************************************************

NOTE: The following list paragraph is included only

when the NIAGARA FRAMEWORK tailoring option is

selected.

**************************************************************************

c. The M&C software must support Niagara Framework Alarm Classes.

d. The M&C software must support at least two alarm priority levels:

critical and informational. Critical alarms must remain in alarm

until acknowledged by an operator and the alarm condition no longer

exists; informational alarms must remain in alarm until the alarm

condition no longer exists or until the alarm is acknowledged.

e. The creation, modification, and handling (routing) of alarms must be

fully accessible and fully adjustable from the graphical user

interface.

f. Alarm Data. Alarm data to be displayed and stored must include:

(1) Identification of alarm including building, system (or

sub-system), and device name.

(2) Date and time to the nearest second of occurrence.

(3) Alarm type:

(a) Unreliable: Indicates that the source device has failed due

to the sensing device or alarm parameter being out-of-range or bad

data.

(b) High Alarm.

SECTION 25 10 10 Page 65

(c) Low Alarm.

(4) Current value or status of the alarm point, including engineering

units

(5) Alarm limits, including engineering units.

(6) Alarm priority.

(7) Alarm Message: A unique message with a field of at least 60

characters. Assignment of messages to an alarm must be an

operator editable function.

(8) Acknowledgement status of the alarm including the time, date and

user of acknowledgement.

**************************************************************************

NOTE: The following list paragraph uses tailoring

options:

1) "ASHRAE 135 event notification" is included when

the BACNET tailoring option is selected.

2) "network variable of type SNVT_alarm or

SNVT_alarm_2" is included when the LONWORKS

tailoring option is selected

3) "OPC alarm" is included when the OPC tailoring

option is selected

4) "or upon generation of an alarm" is included when

the LONWORKS, MODBUS or OPC tailoring option is

selected.

**************************************************************************

g. Alarm Notification and Routing: The M&C software must be capable of

performing alarm notification and routing functions. Upon receipt of

ASHRAE 135 event notification, network variable of type SNVT_alarm or

SNVT_alarm_2, OPC alarm, or upon generation of an alarm the M&C

software must immediately perform alarm notification and routing

according to an assigned routing for that alarm. The M&C software

must support at least 100 alarm routes, where an alarm route is a

unique combination of any of the following activities:

(1) Generate a pop-up up active clients. The pop-up display must

include the Alarm Data. Alarms must be capable of being

acknowledged from the pop-up display by operators with sufficient

permissions. Pop-up must be displayed until acknowledged.

(2) Send an e-mail message via simple mail transfer protocol (SMTP;

RFC 821). The e-mail must contain a configurable message and all

alarm data. The e-mail recipient and scripted message must be

user configurable for each alarm route.

(3) Print alarms to designated alarm printers. The printed message

must be the same as the pop-up message.

h. Alarm Display and Acknowledgement. The M&C software must include an

SECTION 25 10 10 Page 66

alarm display. Alarms must be available for display at each

workstation as shown, along with all associated alarm data. Alarms

must be capable of being acknowledged from this display. Multiple

alarms must be capable of being acknowledged using a single command.

Operator acknowledgment of one alarm must not automatically be

considered as acknowledgment of any other alarm nor may it inhibit

reporting of subsequent alarms.

i. Alarm Storage and Reports: The M&C software must store each alarm and

its associated alarm data to hard disk and retain this information

after the alarm no longer exists. The stored data must be sortable,

searchable, and printable.

2.4.10.14 Trending

**************************************************************************

NOTE: Designer should determine required number of

points M&C software is capable of trending based on

the project site's master plan.

**************************************************************************

**************************************************************************

NOTE: The following list paragraph uses tailoring

options:

1) "of creating, modifying, uploading and archiving

ASHRAE 135 Trend Objects in field devices in

accordance with the B-AWS BIBBs" is included when

the BACNET tailoring option is selected.

2) "of performing real-time trending with a minimum

trending rate of 100 points per second " is included

when the LONWORKS, MODBUS or OPC tailoring option is

selected.

2) "of using the Niagara history service to create,

modify, upload and archive trend log objects in

Niagara Framework Supervisory Gateways" is included

when the NIAGARA FRAMEWORK tailoring option is

selected

**************************************************************************

Provide M&C software capable of creating, modifying, uploading and

archiving ASHRAE 135 Trend Objects in field devices in accordance with the

B-AWS BIBBs and of performing real-time trending with a minimum trending

rate of 100 points per second and of using the Niagara history service to

create, modify, upload and archive trend log objects in Niagara Framework

Supervisory Gateways.

a. The M&C Software must include a graphical display for trend

configuration, creation and deletion accessible through the graphical

user interface. Each trend must be user-configurable for:

(1) Point to trend.

(2) Sampling interval: adjustable between 1 second and 1 hour.

(3) Start and Stop Time of Trend: Start and stop times determined by

one or more of the following methods:

(a) Start time and stop time

SECTION 25 10 10 Page 67

(b) Start time and duration

(c) Start time and number of samples

b. The M&C software must be capable of displaying and printing a

graphical representation of each trend, and of multiple trended points

on the same graph. The software must be capable of saving trend logs

to a file. If the file format is not plain ASCII text in a

Comma-Separated-Value (CSV) format, provide a means to export or

convert the file to plain ASCII text in a CSV format.

2.4.10.15 Electrical Power Demand Limiting

**************************************************************************

NOTE: The critical alarm for actual demand

exceeding the Electrical Demand Target (EDT) should

be routed such that it is received as soon as

possible.

Designer must decide if actual demand exceeding EDT

causes the EDT to be reset to a higher value.

The billing structure should be obtained from the

utility supplying electrical service in order to

coordinate equipment demand limit priorities with

the project site's Energy Manager.

If real-time pricing is a part of the billing

structure it will require coordination with the

demand limiting program. Also, real-time pricing

will require a connection to the Internet to obtain

the pricing information from the utility. This

connection may not exist and may be difficult or

impossible to obtain due to Information Assurance

requirements.

**************************************************************************

Provide M&C software which includes demand limiting functionality capable

of performing electrical demand limiting such that it can change the

occupancy mode or setpoint of field control system hardware via a network

point based on a projected demand in order to maintain demand below a

configured target.[ The demand target must incorporate real-time pricing

data.] The demand limiting algorithm must incorporate priority levels

such that low priority equipment is adjusted before high-priority

equipment. The demand limiting algorithm must generate a critical alarm

when it begins to impact the system and a critical alarm if the demand

target is exceeded.

2.4.10.16 Report Generation

**************************************************************************

NOTE: The list of standard reports should be edited

by the designer to remove any reports or sub-items

of individual reports not required by the project.

**************************************************************************

Provide M&C Software capable of generating, saving and printing reports.

Dynamic operation of the system must not be interrupted to generate a

SECTION 25 10 10 Page 68

report. The report must contain the time and date when the samples were

taken, and the time and date when the report was generated. The software

must be capable of saving reports to a PDF file and to a file compatible

with the provided Office Automation Software.

The software must allow for automatic and manual generation of reports.

For automatic reports an operator must be able to specify the time the

initial report is to be generated, the time interval between reports, end

of period, and the output format for the report. Manual report generation

must allow for the operator to request at any time the output of any

report.

2.4.10.17 Custom Report Generation

Provide M&C software capable of generating custom reports, including but

not limited to the following standard reports:

2.4.10.17.1 Electrical Power Usage Report

An electrical power Usage summary, operator selectable for substations,

meters, or transducers, individual meters and transducers, any group of

meters and transducers, and all meters for an operator selected time

period. The report must include the voltage, current, power factor,

electrical demand, electrical power consumption, reactive power (Kvar) for

each substation, facility, system or equipment as selected by the

operator. The report must be automatically printed at the end of each

summary period and include:

a. Total period consumption.

b. Demand interval peak for the period, with time of occurrence.

c. Energy consumption (kWh) over each demand interval.

d. Time-of-use peak, semi-peak, off-peak, or baseline total kWh

consumption.

e. Reactive power during each demand interval.

f. Power factor during each demand interval.

g. Outside air (OA) temperature and relative humidity (RH) taken at the

maximum and minimum of OA temperature of the report period with the

time and dates of occurrence. At the installation's peak demand

interval, the OA temperature and RH must also be recorded.

h. Calculated heating and cooling degree days based on a 18.3 degrees C

65 degrees F balance point.

2.4.10.17.2 Electrical Peak Demand Prediction Report

A report based on the demand limiting program, which includes:

a. Electrical Demand Target (EDT).

b. Actual peak and predicted peak for each demand interval for that day.

c. Predicted demand for the next demand interval.

SECTION 25 10 10 Page 69

2.4.10.17.3 Energy usage Report

An energy usage summary, operator selectable, for a unit, building, area,

installation, and the entire UMCS. The report must be divided by utility,

and must be capable of reporting on at least four separate utilities. The

report must include the following information:

a. Beginning and ending dates and times.

b. Total energy usage for each utility for the current and previous day.

c. Total energy usage for each utility for the current and previous month.

d. Maximum 15-minute interval average rate of consumption for each

utility for the current and previous day and current and previous

month.

e. Outside air (OA) temperature and OA humidity for current and previous

month and current and previous day:

(1) Average temperature and humidity.

(2) Temperature and humidity at maximum and minimum OA temperature

with time and date of occurrence.

(3) Temperature and humidity at maximum and minimum humidity with

time and date of occurrence.

(4) Temperature and humidity at the installation's peak demand

interval with the time and date of occurrence

f. Calculated degree days. Reports which include humidity must be

configurable to report either dewpoint or relative humidity.

2.4.10.17.4 Water Usage Report

A water usage summary, operator selectable, for a unit, building, area,

installation, and the entire UMCS. The report must include the following

information:

a. Beginning and ending dates and times.

b. Total energy water usage for the current and previous day.

c. Total water usage for the current and previous month.

2.4.10.17.5 Alarm Report

Outstanding alarms by building or unit, including time of occurrence.

2.4.10.17.6 M&C Software Override Report

Points overridden by the M&C Software, including time overridden, and

identification of operator overriding the point.

2.4.10.17.7 Run Time Reports

A report totalizing the accumulated run time of individual pieces of

equipment. The operator must be able to define equipment groupings and to

SECTION 25 10 10 Page 70

generate reports based on these groupings.

2.4.10.17.8 Cooling Tower Profiles

A cooling tower profile for each cooling tower as indicated, including:

a. Total daily and monthly on-time (each fan).

b. Number of on and off transitions (each fan).

c. Maximum and minimum daily condenser water temperature and the time of

occurrence for the current and previous months.

d. Total daily and monthly makeup water consumption.

2.4.10.17.9 Chiller usage Report

A report of the operation of each chiller as shown on a daily and monthly

basis, for each of at least 10 discrete loading levels. The report must

include:

a. Average power for the month at each level in kW

b. Total monthly energy use in kWh at each level

c. Total monthly energy use in kWh for the chiller (all levels)

d. Total daily run hours at each level

e. Total Monthly run hours at each level

2.4.10.17.10 Device Offline Report

**************************************************************************

NOTE: This subpart is included when the BACNET,

LONWORKS or NIAGARA FRAMEWORK tailoring option is

selected and uses tailoring options:

1)"CEA-709.1-D" is included if the LONWORKS

tailoring option is selected

2) "ASHRAE 135" is included if the BACNET tailoring

option is selected.

3) "all offline Niagara Framework Supervisory

Gateways" is included if the NIAGARA FRAMEWORK

tailoring option is selected

**************************************************************************

A report listing all offline devices in all CEA-709.1-D or ASHRAE 135

building control systems integrated to the M&C Software and all offline

Niagara Framework Supervisory Gateways.

2.5 UNINTERRUPTIBLE POWER SUPPLY (UPS)

Provide uninterruptible power supplies (UPS) as self-contained devices

suitable for installation and operation at the location of Server and

Workstation hardware and sized to provide a minimum of 20 minutes of

SECTION 25 10 10 Page 71

operation of the connected hardware. Equipment connected to the UPS must

not be affected in any manner by a power outage of a duration less than

the rated capacity of the UPS. Provide the UPS complete with all

necessary power supplies, transformers, batteries, and accessories.

Provide UPS which include visual indication of normal power operation,

UPS operation, abnormal operation and visual and audible indication of AC

input loss and low battery power. Provide UL 1778 approved UPS. UPS

powering Server Hardware must notify the server via USB interface of

impending battery failure.

2.6 RACKS AND ENCLOSURES

2.6.1 Enclosures

**************************************************************************

NOTE: NOTE: In outdoor applications specify Type 3

unless hosedown of the enclosure is anticipated, in

which case specify Type 4.

For retrofit projects in older mechanical rooms or

where hosedown of the enclosure is anticipated

specify Type 4 enclosures. Type 4 provides a

greater degree of protection in dirty and wet

environments than does Type 2.

**************************************************************************

Enclosures supplied as an integral (pre-packaged) part of another product

are acceptable. Provide two Enclosure Keys for each lockable enclosure on

a single ring per enclosure with a tag identifying the enclosure the keys

operate. Provide enclosures meeting the following minimum requirements:

2.6.1.1 Outdoors

For enclosures located outdoors, provide enclosures meeting NEMA 250 [Type

3][Type 4] requirements.

2.6.1.2 Mechanical and Electrical Rooms

For enclosures located in mechanical or electrical rooms, provide

enclosures meeting NEMA 250 [Type 2][Type 4] requirements.

2.6.1.3 Other Locations

For enclosures in other locations including but not limited to occupied

spaces, above ceilings, and in plenum returns, provide enclosures meeting

NEMA 250 Type 1 requirements.

2.6.2 Equipment Racks

Provide standard 482 mm 19-inch equipment racks compatible with the

electronic equipment provided. Racks must be either aluminum or steel

with bolted or welded construction. Steel equipment racks must be painted

with a flame-retardant paint. Guard rails must be included with each

equipment rack and have a copper grounding bar installed and grounded to

the earth.

PART 3 EXECUTION

**************************************************************************

SECTION 25 10 10 Page 72

NOTE: Determine the applicability and need for a

Factory Test and remove the Factory Test

requirements if a Factory Test is not needed.

For Army projects, contact the UMCS MCX (Huntsville

Center) for a list of systems which have already

been through a Factory Test.

**************************************************************************

[3.1 FACTORY TEST

**************************************************************************

NOTE: Include the reference to section 25 08 10

UTILITY MONITORING AND CONTROL SYSTEM TESTING if

appropriate. Otherwise indicate another basis for

the Factory Test Procedures.

**************************************************************************

Perform factory testing of the UMCS as specified. The Contractor is

responsible for providing personnel, equipment, instrumentation, and

supplies necessary to perform required testing. Provide written

notification of planned testing to the Government at least 21 days prior

to testing, and do not give this notice until after receiving written

Government approval of the specific Factory Test Procedures. Provide

Factory Test Procedures which define the tests required to ensure that the

system meets technical, operational, and performance specifications.

Within the Procedures define location of tests, milestones for the tests,

and identify simulation programs, equipment, personnel, facilities, and

supplies required. Provide procedures which test all capabilities and

functions specified and indicated. Develop Procedures from the design

documentation and in accordance with [Section 25 08 10 UTILITY MONITORING

AND CONTROL SYSTEM TESTING][____]. Perform the Factory Test using

equipment and software of the same manufacturer, model and revision as

will be used for the specified project. Include detailed instructions for

test setup, execution, and evaluation of test results in the Procedures.

Upon completion of the test, prepare a Factory Test Report, documenting

the results of the Test, and submit it as specified.

Perform the Factory Test and provide Factory Test Submittals as shown in

TABLE II. FACTORY TEST SEQUENCING.

TABLE II. FACTORY TEST SEQUENCING

ITEM # DESCRIPTION

SEQUENCING

(START OF ACTIVITY or

DEADLINE FOR SUBMITTAL)

1 Submit Factory Test Procedures [[_____] days after notice to

proceed][_____]

2 Perform Factory Test After Approval Of #1

3 Submit Factory Test Report [_____] days After Completion Of #2

SECTION 25 10 10 Page 73

]3.2 EXISTING CONDITIONS SURVEY

Perform a field survey, including but not limited to testing and

inspection of equipment to be part of the UMCS, and submit an Existing

Conditions Report documenting the current status and its impact on the

Contractor's ability to meet this specification. For field control

systems to be integrated to the UMCS which are not already connected to

the UMCS IP network, verify the availability of the building network

backbone at the FPOC location, and verify that FPOCs shown as existing are

installed at the FPOC location.

3.3 DRAWINGS AND CALCULATIONS

3.3.1 UMCS IP Network Bandwidth Usage Estimate

Provide a UMCS IP Network Bandwidth Usage Estimate for a small, medium or

large systems. In this estimate account for field control systems using

all M&C required protocols and the integration of field control system via

gateways. Define all assumptions used to create the estimate, including

but not limited to: trending, fast trends for commissioning, schedules,

alarms, display of system graphics and load shedding.

3.3.2 Certificate of Networthiness Documentation

**************************************************************************

NOTE: This subpart is only required for Army

projects and is only included when the ARMY

tailoring option is selected.

**************************************************************************

**************************************************************************

NOTE: Include a copy of a blank Certificate of

Networthiness (CoN) "Application Checklist" in the

contract package. This document is available at

https://army.deps.mil/netcom/sites/nw/CoNApproval/Lists/Networthiness%20Data/NWPublicView.(Note that this page may require CAC login)

**************************************************************************

For all software provided, provide documentation that an Enterprise

Certificate of Networthiness exists, that a Limited Certificate of

Networthiness applicable to the project site exists, or provide a

completed Certificate of Networthiness "Application Checklist".

3.3.3 UMCS Contractor Design Drawings

Revise and update the Contract Drawings to include details of the system

design and all hardware components, including contractor provided and

Government furnished components. Details to be shown on the Design

Drawing include:

**************************************************************************

NOTE: The following list paragraph uses tailoring

options:

1) "BACnet Supervisory Controller" is included only

if the BACNET tailoring option is selected

2) "Niagara Framework Supervisory Gateway" is

included only if the NIAGARA FRAMEWORK tailoring

SECTION 25 10 10 Page 74

option is selected.

**************************************************************************

a. The logical structure of the network, including but not limited to the

location of all Control Hardware (including but not limited to each

BACnet Supervisory Controller, Control Protocol Gateway, Control

Protocol Router, Niagara Framework Supervisory Gateway and Monitoring

and Control (M&C) Controller).

b. Manufacturer and model number for each piece of Computer Hardware and

Control Hardware.

c. Physical location for each piece of Computer Hardware and Control

Hardware.

d. Version and service pack number for all software and for all Control

Hardware firmware.

3.3.4 As-Built Drawings

**************************************************************************

NOTE: The Points Schedule is a submittal from

Section 23 09 00 INSTRUMENTATION AND CONTROL FOR

HVAC contracts and is a contract drawing for this

Section. The Contractor updates the Points Schedule

and submits it as an as-built.

Where projects require integration to systems not

installed under Section 23 09 00 INSTRUMENTATION AND

CONTROL FOR HVAC, or where the Points Schedules for

the system are not available, create Points

Schedules for inclusion in the Contract Drawings.

**************************************************************************

Prepare draft as-built drawings consisting of Points Schedule drawings for

the entire UMCS, including Points Schedules for each Gateway, and an

updated Design Drawing including details of the actual installed system as

it is at the conclusion of Start-Up and Start-Up Testing. Provide

As-Built Drawings which include details of all hardware components,

including contractor provided and Government furnished components. In

addition to the details shown in the design drawings, the as-built drawing

must include:

**************************************************************************

NOTE: The following paragraph uses tailoring

options:

1) "BACnet Supervisory Controller" is included only

when the BACNET tailoring option is selected.

2) "Niagara Framework Supervisory Gateway" is

included only when the NIAGARA FRAMEWORK tailoring

option is selected.

**************************************************************************

a. IP address(es) and Ethernet MAC address(es) as applicable for each

piece of Control Hardware (including but not limited to each BACnet

Supervisory Controller, Niagara Framework Supervisory Gateway, Control

Protocol Gateway, Control Protocol Router, and Monitoring and Control

(M&C) Controller).

SECTION 25 10 10 Page 75

b. IP address and Ethernet MAC address for each computer server,

workstation, and networked printer.

c. Network identifier (name) for each printer, computer server and

computer workstation.

d. List of ports, protocols and network services for each device

connected to an IP network.

**************************************************************************

NOTE: The following paragraph uses tailoring

options for BACNET, LONWORKS, MODBUS and NIAGARA

FRAMEWORK and includes requirements only when the

associated tailoring option is selected.

**************************************************************************

e. Network Addresses: CEA-709.1-D address (domain, subnet, node address)

for all Control Hardware using CEA-709.1-D.ASHRAE 135 address and

Object_ID of the Device Object for all Control Hardware using

ASHRAE 135. MODBUS Protocol/MODBUS TCP/IP address for all Control

Hardware using MODBUS Protocol/MODBUS TCP/IP. Niagara Framework

Station ID for all Niagara Framework components including but not

limited to Niagara Framework Supervisory Gateways and the Web

Supervisor.

Prepare Draft As-Built Drawings upon the completion of Start-Up and

Start-Up Testing and Final As-Built Drawings upon completion of PVT Phase

II.

3.4 INSTALLATION REQUIREMENTS

3.4.1 General

**************************************************************************

NOTE: Indicate the location of telecommunications

closets on the contract drawings.

**************************************************************************

Install system components as shown and specified and in accordance with

the manufacturer's instructions and provide necessary interconnections,

services, and adjustments required for a complete and operable system.

Install communication equipment and cable grounding as necessary to

preclude ground loops, noise, and surges from adversely affecting system

operation. Install Fiber Optic cables and wiring in exposed areas,

including low voltage wiring but not including network cable in

telecommunication closets, in metallic raceways or EMT conduit as

specified in Section 26 20 00 INTERIOR DISTRIBUTION SYSTEM. Do not

install equipment in any space which experiences temperatures or humidity

outside of the rated operating range of the equipment.

3.4.2 Isolation, Building Penetrations and Equipment Clearance

Provide dielectric isolation where dissimilar metals are used for

connection and support. Make all penetrations through and mounting holes

in the building exteriors watertight. Drill or core drill holes in

concrete, brick, steel and wood walls with proper equipment. Seal

conduits installed through openings with materials which are compatible

with existing materials. Seal openings with materials which meet the

requirements of NFPA 70 and SECTION 07 84 00 FIRESTOPPING.

SECTION 25 10 10 Page 76

3.4.3 Nameplates

Provide Nameplates for all Control Hardware and all Computer Hardware.

Attach Nameplates to the device in a conspicuous location.

3.5 INSTALLATION OF EQUIPMENT

3.5.1 Wire and Cable Installation

Install system components and appurtenances in accordance with NFPA 70,

manufacturer's instructions and as indicated. Provide necessary

interconnections, services, and adjustments required for a complete and

operable signal distribution system. Label components in accordance with

TIA-606. Firestop Penetrations in fire-rated construction in accordance

with Section 07 84 00 FIRESTOPPING. Install conduits, outlets and

raceways in accordance with Section 26 20 00 INTERIOR DISTRIBUTION

SYSTEM. Install wiring in accordance with TIA-568-C.1 and as specified in

Section 26 20 00 INTERIOR DISTRIBUTION SYSTEM. Mark wiring terminal

blocks and outlets in accordance with TIA-606. Do not install

non-fiber-optic cables in the same cable tray, utility pole compartment,

or floor trench compartment with power cables. Properly secure and

install neat in appearance cables not installed in conduit or raceways.

3.5.2 Grounding

Install signal distribution system ground in accordance with TIA-607 and

Section 26 20 00 INTERIOR DISTRIBUTION SYSTEM. Connect equipment racks to

the electrical safety ground.

3.5.3 Power-Line Surge Protection

Protect equipment connected to ac circuits must be protected against or

withstand power-line surges. Provide equipment protection which meets the

requirements of IEEE C62.41. Do not use fuses for surge protection.

3.5.4 IP Addresses

**************************************************************************

NOTE: Select the appropriate option to do one of

the following:

1) require the contractor to coordinate IP Addresses

with NEC (the IT group)

2) require the contractor use IP addresses from a

list of supplied IP addresses. In this case,

include a list of IP addresses.

3)(not applicable to Air Force) require the

contractor to configure control hardware to obtain

IP addresses from a DHCP server.

**************************************************************************

For all Control Hardware requiring an IP address on the UMCS IP Network,

[coordinate with the [NEC] [_____] to obtain IP addresses] [use the

following IP addresses:[_____]][obtain static IP addresses from a DHCP

server].

SECTION 25 10 10 Page 77

3.5.5 Computer Hardware and Software

**************************************************************************

NOTE: If computer hardware is Government installed

remove the bracketed text requiring hardware

installation.

**************************************************************************

[3.5.5.1 Hardware Installation

Install Computer Hardware as specified and indicated. Power Computer

Servers through a UPS, and install and configure them such that the server

automatically undergoes a clean shutdown upon low battery signal from the

UPS.

]3.5.5.2 Software Installation

Install software as follows:

**************************************************************************

NOTE: Due to tailoring options the numbering of the

following items may be incorrect and require editing.

**************************************************************************

**************************************************************************

NOTE: The following TWO list paragraphs are included

only if the LONWORKS tailoring option is selected

**************************************************************************

a. CEA-852-C Configuration Server: Install and configure one CEA-852-C

Configuration Server. Install the he CEA-852-C Configuration Server

on Server Hardware or on an CEA-709.1-D TP/FT-10 to IP Router.

b. CEA-709.1-D Network Configuration Tool: Install the CEA-709.1-D

Network Configuration Tool software as shown. Install the CEA-709.1-D

Network Configuration Tool on workstation or server hardware.

**************************************************************************

NOTE: The following designer note and list paragraph

are included only if the BACNET tailoring option is

selected

**************************************************************************

**************************************************************************

NOTE: The BACnet Network Browser may or may not be

needed by the installation. The M&C Software

already has this functionality, but in general a

copy of a BACnet Network Browser installed on a

laptop is beneficial for the installation for O&M,

troubleshooting and commissioning.

Keep the bracketed option and show the BACnet

Network Browser on the drawings to require it.

**************************************************************************

[ c. BACnet Network Browser: Install the BACnet Network Browser software as

indicated. Install the BACnet Network Browser on workstation hardware.

]

SECTION 25 10 10 Page 78

**************************************************************************

NOTE: The following designer note and list paragraph

are included only if the NIAGARA FRAMEWORK

tailoring option is selected

**************************************************************************

**************************************************************************

NOTE: The Niagara Framework Engineering Tool must

be installed on the Web Supervisor. It may or may

not need to be installed on more than the Web

Supervisor server.

Keep the bracketed option and show the Niagara

Framework Engineering Tool on the drawings to

require it to be installed on more the Web

Supervisor server.

**************************************************************************

d. Niagara Framework Engineering Tool: Install the Niagara Framework

Engineering Tool on the Web Supervisor Server[ and as indicated.

Install the Niagara Framework Engineering Tool on workstation

hardware].

**************************************************************************

NOTE: The following list paragraph uses tailoring

options.

The sentence "Install M&C Software in a manner

consistent with its B-AWS listing such that it

provides all functionality of a B-AWS." is included

only if the BACNET tailoring option is selected

**************************************************************************

e. Monitoring and Control Software: Install the monitoring and control

(M&C)software as shown. Except for M&C Software performing Point

Calculations or Electrical Peak Demand Limiting, install M&C Software

on server hardware. Install M&C Software performing Point

Calculations or Electrical Peak Demand Limiting on either server

hardware or Monitoring and Control (M&C) Controller Hardware. Install

M&C Software in a manner consistent with its B-AWS listing such that

it provides all functionality of a B-AWS.

Provide sufficient computer hardware and M&C Controller Hardware and

install M&C Software to support the number of points required in PART

2 (PRODUCTS), regardless of the number of points integrated under this

project specification. Note that meeting this requirement may entail

the installation of unused hardware or spare point licenses to

accommodate the full number of required points in order to allow for

integration of future field control systems.

f. M&C Controller Hardware Configuration Software: Install the M&C

Controller Hardware Configuration Software on server hardware.

**************************************************************************

NOTE: Remove the bracketed text if the software is

Government installed. Coordinate with the project

site and project site IT organization to determine

which software will be Government installed, and to

determine the information required to complete the

SECTION 25 10 10 Page 79

brackets.

Note that if some software is Government installed

but others are required the items may need to be

renumbered.

If the Operating System is installed by the

contractor provide a point of contact for user names

and passwords.

If the Virus Protection Software is installed by the

contractor indicate whether an update server is

available and provide server information or a POC to

obtain server information.

**************************************************************************

[ g. Operating system: Install the OS on each Server and Workstation and

configure user names and passwords. Coordinate with [____] for user

names and passwords.

][h. Office Automation Software: Install the office automation software on

each server and workstation.

][i. Virus Protection software: Install the virus protection software on

each server and workstation and configure weekly virus scans.

[Configure the virus protection software to update virus definitions

automatically [from the update server at [____]][. Coordinate with

[the NEC][____] to obtain update server information.]]

][j. Disk Imaging (Backup) Software: Install the disk imaging (backup)

software on each server and configure for imaging the internal hard

drive to external hard drive.]

**************************************************************************

NOTE: Indicate who to coordinate with to get

connections outside of the UMCS. Note that

connections to non-government servers are not

required by the UMCS and should not be permitted.

**************************************************************************

Where software requires connection to an IP device outside of the UMCS,

coordinate with [the project site NEC][____] to obtain access to a

Government-furnished server to provide the needed functionality. Do not

connect to any device outside of the UMCS without explicit permission from

[the project site NEC][____].

3.5.5.3 Monitoring and Control (M&C) Software Configuration

Configure the Monitoring and Control (M&C) Software as specified, as

indicated and as follows:

**************************************************************************

NOTE: Indicate who to coordinate user accounts with.

If in the product section you selected that the M&C

software uses Windows for user authentication then

remove the bracketed text (3 places) concerning

passwords. Otherwise keep the bracketed text

SECTION 25 10 10 Page 80

concerning passwords.

**************************************************************************

a. Set up M&C Software user accounts[ and passwords]. Coordinate user

accounts[, passwords] and permissions with [the [Controls] [HVAC]

[Electrical] shop supervisor][____].

b. Change the default password on all accounts. Remove or disable any

accounts which do not require authentication (such as guest accounts).

**************************************************************************

NOTE: Either provide SMTP (e-mail) server

information or a POC for the contractor to obtain

this information.

**************************************************************************

c. Configure e-mail capability to use [the government furnished SMTP

server using the following server information[____].][a Government

furnished SMTP server. Coordinate with [the project site NEC]

[____]for SMTP server information.]

d. Disable all ports, protocols, and network services other than those

required or specifically permitted by this Section. Services to be

disabled include but are not limited to: FTP, Telnet and SSH.

**************************************************************************

NOTE: Indicate where contractor should obtain

certificate.

**************************************************************************

e. Install web server certificate. Obtain certificate from [the project

site NEC][____].

3.5.5.4 Control Hardware Installation

**************************************************************************

NOTE: Select if Control Hardware must be installed

in an enclosure. Hardware in telecommunication

closets will generally not require an enclosure

unless necessary to secure the Hardware (i.e. a

locked enclosure).

FYI - the requirements for which (if any) Control

Hardware to install and where to install it is

covered below in the integration requirements.

If permitting Niagara Framework Supervisory Gateways

to serve web pages, keep the bracketed text allowing

HTTP from Niagara Framework Supervisory Gateways.

**************************************************************************

Install Control Hardware [in an enclosure] [in a lockable enclosure] and

as specified. Configure Control Hardware as specified, as required to meet

the functions for which the hardware is used and as follows:

**************************************************************************

NOTE: The following list paragraph uses tailoring

options.

SECTION 25 10 10 Page 81

The text "[ except for HTTP originating in Niagara

Framework Supervisory Gateways]" is included only if

the NIAGARA FRAMEWORK tailoring option is selected.

**************************************************************************

a. Disable all ports, protocols, and network services other than those

required or specifically permitted by this Section. Services to be

disabled include but are not limited to: FTP, Telnet, SSH, and HTTP[

except for HTTP originating in Niagara Framework Supervisory Gateways].

When disabling of ports, protocols and services is not supported by a

product, obtain an exception from this requirement prior to using the

product and document non-compliance on the Product Data Sheets and

As-Built drawings.

**************************************************************************

NOTE: Indicate who the contractor should coordinate

with to determine passwords.

**************************************************************************

b. Change the default passwords in all Control Hardware which have

passwords. Coordinate new passwords with [the [Controls] [HVAC]

[Electrical] shop supervisor][____].

3.6 INTEGRATION OF FIELD CONTROL SYSTEMS

**************************************************************************

NOTE: For complete integration the contract package

must include the following:

1. Points Schedule - make sure Points Schedule

includes:

- points to be displayed by the M&C

Software

- points that can be overridden by the M&C

Software

- trend points.

- Alarm routing (also make sure to include the

Alarm Routing Schedule)

2. Alarm Routing Schedule drawings.

Identify and assign priorities, e-mail

addresses (for e-mail and text notification),

and alarms to be printed.

3. Demand Limit schedule drawing.

Make sure it includes system name, load shed

priority and point needed for shut-down or

setpoint reset.

4. Control System Schematics for each field

control system (This may be an as-built

drawing from the field control system

specification - such as Section 23 09 00

INSTRUMENTATION AND CONTROL FOR HVAC)

5. Occupancy Schedules for each field control

system. (This may be an as-built drawing

from the field control system specification -

such as Section 23 09 00 INSTRUMENTATION AND

SECTION 25 10 10 Page 82

CONTROL FOR HVAC)

While integration *may* be able to be performed

without the other drawings, the Points Schedule is

required for successful integration of any system

and must be provided.

Note that the necessary Points Schedule drawing

should be part of the as-built submittal for

building control systems - particularly those

installed using Section 23 09 00 INSTRUMENTATION AND

CONTROL FOR HVAC. If a points schedule for the

system is not available one must be created and

included in the contract package. Alternatively, a

requirement can be manually added here (along with

appropriate edits to the submittals and project

sequencing paragraphs) to include a site survey of

the system prior to integration, the results of

which the Government must then use to provide actual

integration requirements such as identifying points

to be displayed, overridden, trended etc (thus

creating a Points Schedule as part of the project).

**************************************************************************

**************************************************************************

NOTE: Contract drawings must indicate the FPOC

location or FPOC location must be provided in the

empty bracket.

Coordinate with the project site to ensure there is

an FPOC available for connection of the building

control network to the UMCS IP Network..

**************************************************************************

Fully integrate the field control systems in accordance with the following

three step sequence and as specified and shown.

STEP 1: Install and configure Control Hardware as necessary to connect

the field control system to the FPOC, which is part of the UMCS IP

network, and to provide control protocol translation and supervisory

functionality.

STEP 2: Add Field Control System to M&C Software: Perform system

discovery, system database merges, or any other actions necessary to

allow M&C Software access to the field control system.

STEP 3: Configure M&C Software to provide monitoring and control of the

field control system, including but not limited to the creation of

system displays and the configuration of scheduling, alarming, and

trending.

3.6.1 Integration Step 1: Install Control Hardware

**************************************************************************

NOTE: Step 1 requires connecting to the FPOC, which

is typically managed by the project site IT staff.

Provide a POC for making this connection.

**************************************************************************

SECTION 25 10 10 Page 83

Install Control Hardware as specified at the FPOC location [as

shown][____] to connect the field control system to the UMCS IP network

via the FPOC and, if necessary, to provide control protocol translation

and supervisory functionality. Coordinate all connections and other

activities related to an FPOC with [____]. Depending on the field control

system media and protocol this must be accomplished through one of the

following:

a. Connect the existing field control network hardware at the FPOC

location to the FPOC.

**************************************************************************

NOTE: The following list paragraph uses tailoring

options.

1) "Control Protocol Gateway" is included if the

BACNET, LONWORKS, MODBUS or OPC tailoring option is

selected.

2) "Niagara Framework Supervisory Gateway" is

included if the NIAGARA FRAMEWORK tailoring option

is selected.

3) The "either" and "or" are included if the NIAGARA

FRAMEWORK tailoring option AND any of the other 4

protocol tailoring options are selected.

**************************************************************************

b. Install either a Control Protocol Gateway or Niagara Framework

Supervisory Gateway connected to both the field control network and

the FPOC.

**************************************************************************

NOTE: The following TWO list paragraphs are included

if the BACNET, LONWORKS, MODBUS or OPC tailoring

option is selected.

**************************************************************************

c. Install a Control Protocol Router connected to both the field control

network and the FPOC.

d. Install a Control Protocol Gateway connected to the field control

network. Then install a Control Protocol Router connected to both the

Control Protocol Gateway and the FPOC.

**************************************************************************

NOTE: The following paragraph is included if the

BACNET tailoring option is selected.

**************************************************************************

In addition, for integration of field control systems via ASHRAE 135, also

install a BACnet Supervisory Controller as needed to implement scheduling,

alarming and trending in the field control system. The BACnet

supervisory controller may be the same device as the control protocol

gateway or router.

SECTION 25 10 10 Page 84

3.6.1.1 Installation of Control Protocol Gateway

**************************************************************************

NOTE: This subpart is included only if the BACNET,

LONWORKS, MODBUS or OPC tailoring option is selected.

This subpart also uses tailoring options to:

1) include the references to the protocol only if

the corresponding tailoring option is selected

2) include the protocol routers only when the

corresponding tailoring option is selected

**************************************************************************

If the field control system uses a protocol which is not supported by the

M&C Software, install a gateway to convert the field control system

protocol to ASHRAE 135, or to CEA-709.1-D, or to MODBUS Protocol/

MODBUS TCP/IP, or to OPC DA. Install additional field control system

network media and hardware as needed to connect the Gateway to the field

control system. Connect the Gateway according to one of the two following

methods:

a. Connect the Gateway to the field control network and to the FPOC. .

b. Connect the Gateway to the field control network and to a BACnet/IP

Router, or to a LonWorks/IP Router, or to a Modbus/IP Router installed

as specified.

Create and configure points and establish network communication between

the Control Protocol Gateway and the field control system to provide

points from the field control system to the M&C software.

3.6.1.2 Installation of Niagara Framework Supervisory Gateway

**************************************************************************

NOTE: This subpart only applies to Niagara

Framework systems and is only included when the

NIAGARA FRAMEWORK tailoring option is selected.

**************************************************************************

Install Niagara Framework Supervisory Gateway hardware to connect the

field control network to the FPOC. Install additional field control

system network media and hardware as needed to connect the Niagara

Framework Supervisory Gateway to the field control system.

3.6.1.3 Installation of Control Protocol Router

**************************************************************************

NOTE: This subpart is included only if the BACNET,

LONWORKS, MODBUS or OPC tailoring option is selected.

This subpart uses tailoring options to include the

protocol routers only when the corresponding

tailoring option is selected

**************************************************************************

If there is not an existing connection between the FPOC and the field

control network, install a BACnet/IP Router, or a LonWorks/IP Router, or a

Modbus/IP Router to connect the field control network to the FPOC.

SECTION 25 10 10 Page 85

Install additional field control system network media as needed to connect

the Router to the field control system.

3.6.1.4 Installation of BACnet Supervisory Controller

**************************************************************************

NOTE: This subpart only applies to BACnet systems

and is only included when the BACNET tailoring

option is selected.

**************************************************************************

If required for implementation of scheduling, alarming and trending,

install a BACnet Supervisory Controller connected to the building control

system IP network and configure it to provide scheduling, alarming and

trending functions for the field control system. When the BACnet

Supervisory Controller is the same device as a control protocol router or

gateway, install it in accordance with the installation requirements for a

router or gateway.

3.6.2 Integration Step 2: Add Field Control System to M&C Software

Perform system discovery, system database merges, or any other actions

necessary to allow M&C Software access to points and data in the field

control system.

3.6.2.1 Integration of Field Control Systems Via ANSI-709.1-C

**************************************************************************

NOTE: This subpart only applies to integration via

LonWorks and is only included when the LONWORKS

tailoring option is selected.

**************************************************************************

a. When a LNS Database of the field control system is not available, use

the Network Configuration Tool software to discover the field control

system and create an LNS Database for the field control system.

b. When the UMCS does not already contain an LNS Server, provide an LNS

Server to support the UMCS LNS Database.

c. When there is no existing UMCS LNS Database, use the field control

system database as the UMCS Database.

d. When there is an existing UMCS LNS Database, merge the field control

system with the UMCS LNS database.

3.6.2.2 Integration of Field Control Systems Via ASHRAE 135

**************************************************************************

NOTE: This subpart only applies to integration via

BACnet and is only included when the BACNET

tailoring option is selected.

**************************************************************************

Use the M&C Software to fully discover the field control system. Full

discovery of a field control system includes but is not limited to

discovery of all ASHRAE 135 devices, all standard ASHRAE 135 Objects and

Properties of each device, and all standard ASHRAE 135 services supported

by each device.

SECTION 25 10 10 Page 86

3.6.2.3 Integration of Field Control Systems Via Niagara Framework

**************************************************************************

NOTE: This subpart only applies to integration via

Niagara Framework and is only included when the

NIAGARA FRAMEWORK tailoring option is selected.

**************************************************************************

For each Niagara Framework Supervisory Gateway installed in integration

step 1 for this project do both of the following:

a. Use the Niagara Framework Engineering Tool to fully discover the field

control system and make all field control system information available

to the Niagara Framework Supervisory Gateway.

b. Create and configure points and establish network communication

between the Niagara Framework Supervisory Gateway and the field

control system to provide points from the field control system to the

M&C software and to provide support for supervisory functions,

including but not limited to schedule objects, trend logs and alarming.

For each Niagara Framework Supervisory Gateway to be integrated as part of

this project, make all information in the Niagara Framework Supervisory

Gateway available to the M&C Software.

3.6.2.4 Integration of Field Control Systems Via Modbus

**************************************************************************

NOTE: This subpart only applies to integration via

Modbus and is only included when the MODBUS

tailoring option is selected.

**************************************************************************

**************************************************************************

NOTE: Detailed documentation will be required for

the integration of Modbus systems as there is no

standard database (like there is in LonWorks) or no

standard means for device discovery (like there is

in BACnet).

Keep the first large set of bracketed text if this

point information does not exist and the contractor

must survey the building to determine the

appropriate point information. When using this

option, consider providing a POC at the project site

who can assist the contractor with this survey.

Keep the second large set of bracketed text if this

point information is available, and indicate the

source of this point information:

Use [contract document Points Schedule] if the

Points Schedule exists and will be included in the

contract package

Use [field control system documentation Points

Schedules] if the integrating contractor is also

providing the Modbus system at the same time.

SECTION 25 10 10 Page 87

Use [____] to indicate other ways this information

is being conveyed.

If the points required by the M&C Software (for

display, trends, alarms etc) are shown on a Points

Schedule keep [ as shown on the Points Schedule],

otherwise remove this bracketed text to require all

points be available.

**************************************************************************

[Survey the field control system to create Points Schedules. Using these

Points Schedules ][Using the [contract document Points Schedule][field

control system documentation Points Schedules][____],] make all points[ as

shown on the Points Schedule] from the field control system available in

the M&C Software.

3.6.2.5 Integration of Field Control Systems Via OPC DA

**************************************************************************

NOTE: This subpart only applies to integration via

OPC and is only included when the OPC tailoring

option is selected.

**************************************************************************

**************************************************************************

NOTE: If the points required by the M&C Software

(for display, trends, alarms etc) are shown on a

Points Schedule keep [ as shown on the Points

Schedule], otherwise remove this bracketed text to

require all points be available.

**************************************************************************

Establish a connection between the M&C Software OPC DA client and the

field control system OPC DA server and make all points[ as shown on the

Points Schedule] from the field control system available in the M&C

Software.

3.6.2.6 [Enter Appropriate Subpart Title Here]Integration of Field Control

Systems Via Other (non-Niagara Framework (Fox Protocol), non-ASHRAE 135,

non-CEA-709.1-D, non-Modbus, non-OPC DA) Protocols

**************************************************************************

NOTE: If the points required by the M&C Software

(for display, trends, alarms etc) are shown on a

Points Schedule keep [ as shown on the Points

Schedule], otherwise remove this bracketed text to

require all points be available.

The requirement here for making points available to

the M&C Software are broad since it is not possible

to specify how perform these tasks without details

about the field control system and M&C Software.

**************************************************************************

Perform all actions necessary to make all points[ as shown on the Points

Schedule] from the field control system available in the M&C Software.

SECTION 25 10 10 Page 88

3.6.3 Integration Step 3: Configure M&C Software

Configure M&C Software to provide monitoring and control of the field

control system, including but not limited to the creation of system

displays and the configuration of scheduling, alarming, and trending.

3.6.3.1 Configure M&C Software Communication

Create and configure points and establish network communication between

M&C Software and Field Control Systems as specified to support M&C

Software functionality:

a. Update points on currently active displays via polling as necessary to

meet M&C Software display refresh requirements.

**************************************************************************

NOTE: The following list paragraph uses tailoring

options.

1) LonWorks requirements are included only when the

LONWORKS tailoring option is selected.

2) BACnet requirements are included only when the

BACNET tailoring option is selected.

**************************************************************************

b. Send points used for overrides to the device receiving the override as

shown on the Points Schedule. For LonWorks systems, for points used

for overrides use the network variable and SNVT type indicated on the

Points Schedule. For SNVTs for overriding schedules (via the Simple

Scheduler) use SNVT type SNVT_occupancy and support the following

values: OC_OCCUPIED, OC_UNOCCUPIED, OC_STANDBY and OC_NUL. For SNVTs

used to override schedules or setpoints for Demand Limiting functions

use the acknowledged service. For BACnet systems write operator

overrides with a priority of 8 and demand limiting overrides with a

priority of 10.

**************************************************************************

NOTE: The following list paragraph uses tailoring

options.

1) BACnet requirements are included only when the

BACNET tailoring option is selected.

2) LonWorks requirements are included only when the

LONWORKS tailoring option is selected.

3) MODBUS requirements are included only when the

MODBUS tailoring option is selected.

4) OPC requirements are included only when the OPC

tailoring option is selected.

**************************************************************************

c. For Notification Class Objects used for Alarms, configure the

Recipient_List Property to point to the appropriate M&C Software

process. Use the ConfirmedEventNotification service for events from

ASHRAE 135 field control systems used for alarms. Bind points from

CEA-709.1-D field control systems used using acknowledged service or

poll the point at 5 minute intervals. Poll points from MODBUS Protocol

/MODBUS TCP/IP field control systems used for alarms at 5 minute

intervals. For points from OPC DA field control systems used for

alarms use a subscription or poll the point at 5 minute intervals.

SECTION 25 10 10 Page 89

**************************************************************************

NOTE: The following TWO list paragraphs are

included only when the LONWORKS, MODBUS or OPC

tailoring option is selected.

Requirements for LonWorks field control system are

only included when the LONWORKS tailoring option is

selected.

**************************************************************************

d. Update points used for currently active trends via polling as

necessary to meet trend interval requirements.

e. Send points used for scheduling to the field control system with a

maximum time between subsequent transmissions of the point of 30

minutes. For LonWorks field control systems, send points used for

scheduling to the appropriate System Scheduler using SNVTs of type

SNVT_occupancy which support the following values: OC_OCCUPIED,

OC_UNOCCUPIED and OC_STANDBY.

**************************************************************************

NOTE: Future upward reporting to an enterprise

system will likely require that Real Property Unique

IDs (18 digits numeric) be included when point

information is transmitted to the enterprise. The

following requires that the contractor include the

Real Property Unique IDs (RPUID) in a description

field of the M&C Software point when performing

integration. Coordinate with the project site to

determine whether to include this requirement. If

including this requirement show the RPUID on the

Points Schedule.

**************************************************************************

[ Edit the Description field of each point to include the Real Property

Unique IDs (RPUID) associated with that point as shown on the Points

Schedule

]3.6.3.2 Configure M&C Software Functionality

Fully configure M&C Software functionality using the M&C Software

capabilities specified in PART 2 of this Section.

**************************************************************************

NOTE: Indicate if the installation has sample

graphic pages. Indicate how points on graphic pages

should be labeled. Coordinate with the project site

to determine if they have a naming convention.

Indicate who the contractor should coordinate with

for user permissions.

**************************************************************************

a. Create System Displays [using the [project site] sample displays,

]including overrides, as shown on the Points Schedule and as

specified. Label all points on displays with [full English language

descriptions][the point name as shown on the Points Schedule][the

point description as shown on the Points Schedule][____]. Configure

SECTION 25 10 10 Page 90

user permissions for access to and executions of action using graphic

pages. Coordinate user permissions with [the [Controls] [HVAC]

[Electrical] shop supervisor][____]

**************************************************************************

NOTE: The following list paragraph uses tailoring

options:

1) the phrase "alarm generation and" is included

only when the LONWORKS, MODBUS or OPC tailoring

option is selected.

2) The requirements for configuring alarming in

BACnet ("Create and configure... and all others as

critical.") are included only when the BACNET

tailoring option is selected

**************************************************************************

b. Configure alarm generation and alarm handling as shown on the Points

Schedule, as shown on the Alarm Routing Schedule, and as specified.

Create and configure Objects in BACnet Supervisory Controllers and in

the field control system to support alarming as shown on the Points

Schedule and as specified. Alarm events with priority 112 are

critical and events with priority 224 are non-critical. For alarm

events with other priorities, treat events with priorities of 200 or

above as non-critical, and all others as critical. For alarms

requiring notification via text message or e-mail, configure the alarm

notification to use the specified Government furnished SMTP server to

send the alarm notification.

**************************************************************************

NOTE: The following 2 list paragraphs use tailoring

options to include requirements for the selected

protocol tailoring options only.

**************************************************************************

c. Configure scheduling as indicated and as shown on the points

schedule. Configure M&C Software scheduling functionality to schedule

Modbus systems and OPC systems. Configure M&C Software scheduling

functionality for LonWorks field control systems which do not use the

Simple Scheduler Object. For LonWorks field control systems which do

use the Simple Scheduler Object, configure the Simple Scheduler

Objects in the field control system. Create and configure Schedule

Objects in BACnet Supervisory Controllers or in the field control

system.

Create and configure displays for configuration of M&C Software

schedules and Simple Scheduler Objects in the field control system and

Schedule Objects in the field control system. Label schedules and

scheduled points with full English-language descriptors. Provide a

separate configuration capability for each schedule. A single

configuration display may be used to configured multiple schedules,

provided that each schedule is separately configurable from the

display.

**************************************************************************

NOTE: The following list paragraphs uses tailoring

options:

1) "Create M&C Software trends for required points

as shown on the Points Schedule and as specified."

SECTION 25 10 10 Page 91

is included when the LONWORKS, MODBUS or OPC

tailoring option is selected.

2) "Create and configure Trend Objects in BACnet

Supervisory Controllers and in the field control

system as shown on the Points Schedule and as

specified" is included only when the BACNET

tailoring option is selected.

**************************************************************************

d. Create M&C Software trends for required points as shown on the Points

Schedule and as specified. Create and configure Trend Objects in

BACnet Supervisory Controllers and in the field control system as

shown on the Points Schedule and as specified. Trend points at [15]

[_____] minute intervals.

Create and configure displays for creation and configuration of trends

and for display of all trended points.

e. Configure Demand Limiting as shown on the Demand Limit Schedule and

Points Schedule and as specified.

f. Configure M&C Software standard reports.

3.7 START-UP AND START-UP TESTING

Test all equipment and perform all other tests necessary to ensure the

system is installed and functioning as specified. Prepare a Start-Up and

Start-Up Testing Report documenting all tests performed and their results

and certifying that the system meets the requirements specified in the

contract documents.

3.8 PERFORMANCE VERIFICATION TEST (PVT)

**************************************************************************

NOTE: A set of Field Test Procedures are being

developed by an A/E under contract with Huntsville

Center. Once complete, these Test Procedures will

be included or referenced here.

Brief interim guidance is provided here.

**************************************************************************

3.8.1 PVT Phase I Procedures

Provide PVT Procedures which include:.

a. Network bandwidth usage and available bandwidth (throughput)

measurements. Network bandwidth usage must reference the normal usage

network Bandwidth Calculations.

b. Test System Reaction during PVT: The total system response time from

initiation of a control action command from the workstation, to

display of the resulting status change on the workstation must not

exceed 20 seconds under system normal heavy load conditions assuming a

zero response time for operation of the node's control device.

c. Verification of IP Connectivity.

SECTION 25 10 10 Page 92

d. Verification of configuration of M&C Software functionality.

3.8.2 PVT Phase I

Demonstrate compliance of the control system with the contract documents.

Using test plans and procedures previously approved by the Government,

demonstrate all physical and functional requirements of the project. Upon

completion of PVT Phase I and as specified, prepare and submit the PVT

Phase I Report documenting all tests performed during the PVT and their

results. In the PVT report, include all tests in the PVT Procedures and

any other testing performed during the PVT. Document failures and repairs

with test results.

3.8.3 PVT Phase II

Include Basic Training as part of PVT Phase II. Failures or deficiencies

of the UMCS during Basic Training are considered PVT failures. Upon

completion of PVT Phase II, and as specified, prepare and submit the PVT

Phase II Report documenting any failures which occurred and repairs

performed during PVT Phase II.

3.9 MAINTENANCE AND SERVICE

**************************************************************************

NOTE: The maintenance and service to be provided by

the Contractor for the duration of the IDIQ or

maintenance contract is specified in this

paragraph. The Maintenance and Service may need to

be a separate bid item funded by O&M funds.

Some/many of these Maintenance and Service

requirements may not apply if the UMCS networking

equipment and supporting infrastructure is

Government furnished equipment and maintained by the

Government. The requirements here generally assume

that the contractor is permitted access to the

system and equipment, but the applicability of this

assumption will vary site-by-site. It's critical to

coordinate with the project site to determine to

what extent the contractor will be responsible for

system and equipment maintenance. Some notes have

been included with bracketed text to provide general

guidance, but careful editing of this entire subpart

is needed.

Requirements should be coordinated with "WARRANTY

MANAGEMENT" in Section 01 78 00 CLOSEOUT SUBMITTALS

**************************************************************************

Perform inspection, testing, cleaning, and part or component replacement

as specified and as required to maintain the warranty. Work includes

providing necessary preventive and unscheduled maintenance and repairs to

keep the UMCS operating as specified, and accepted by the Government, and

other services as specified. Perform work in compliance with

manufacturer's recommendations and industry standards. Provide technical

support via telephone during regular working hours.

SECTION 25 10 10 Page 93

3.9.1 Work Coordination

Schedule and arrange work to cause the least interference with the normal

Government business and mission. In those cases where some interference

may be essentially unavoidable, coordinate with the Government to minimize

the impact of the interference, inconvenience, equipment downtime,

interrupted service and personnel discomfort.

3.9.2 Work Control

Upon completion of work on a system or piece of equipment, that system or

piece of equipment must be free of missing components or defects which

would prevent it from functioning as originally intended and designed.

Replacements must conform to the same specifications as the original

equipment. During and at completion of work, do not allow debris to

spread unnecessarily into adjacent areas nor accumulate in the work area

itself.

3.9.3 Working Hours

Working hours are from [7:30 A.M.] [_____] to [4:00 P.M.] [_____] local

time Mondays through Fridays except Federal holidays.

[3.9.4 Equipment Repairs

**************************************************************************

NOTE: Coordinate with the project site to determine

if equipment (computers and control hardware) repair

will be done by the contractor or by local staff,

and to what extent. If the equipment is Government

furnished then the contractor may not be allowed

access to some/all of the equipment for repair.

Address Information Assurance (IA) or other

equipment access requirements in "Access To UMCS

Equipment" below.

Select repair times below.

**************************************************************************

Initiate and complete equipment repairs within the following time periods,

where time periods are measured as actual elapsed time from first

notification, including working and non-working hours:

a. for non-redundant computer server hardware, initiate within [4]

[_____] hours and complete within [8] [_____] hours.

b. for non-redundant computer workstation hardware, initiate within [4]

[_____] hours and complete within [8] [_____] hours.

c. for redundant computer server hardware, initiate within [36] [_____]

hours and complete within [5] [_____] days.

d. for redundant computer workstation hardware, initiate within [2]

[_____] days and complete within [5] [_____] days.

e. for active (powered) control hardware, initiate within [4] [_____]

hours and complete within [6] [_____] hours.

f. for cabling and other passive network hardware, initiate within [16]

SECTION 25 10 10 Page 94

[_____] hours and complete within [5] [_____] days.

Repair is the restoration of a piece of equipment, a system, or a facility

to such condition that it may be effectively used for its designated

purposes. Repair may be overhaul, reprocessing, or replacement of

nonfunctional parts or materials or replacement of the entire unit or

system.

]3.9.5 Replacement, Modernization, Renovation

The Government may replace, renovate, or install new equipment as part of

the UMCS at Government expense and by means not associated with this

contract without voiding the system warranty. Replaced, improved,

updated, modernized, or renovated systems and equipment interfaced to the

system may be added to the Contractor's maintenance and service effort as

a modification.

3.9.6 Access To UMCS Equipment

**************************************************************************

NOTE: Coordinate with the project site to determine

any additional access requirements. Specifically,

computer and/or control hardware access will likely

require meeting certain Information Assurance (IA)

requirements.

**************************************************************************

Access to UMCS equipment must be in accordance with the following:

a. Coordinate access to facilities and arrange that they be opened and

closed during and after the accomplishment of the work effort. For

access to a controlled facility contact the Government for assistance.

b. The Government may provide keys for access to UMCS equipment where the

Government determines such key issuance is appropriate. Establish and

implement methods of ensuring that keys issued by the Government are

not lost or misplaced, are not used by unauthorized persons, and are

not duplicated.

c. The Government may provide passwords or issue Common Access Cards

(CAC) for access to UMCS computer equipment where the Government

determines such issuance is appropriate. Establish and implement

methods of ensuring that passwords and Common Access Cards issued by

the Government are not used by unauthorized persons.

3.9.7 Records, Logs, and Progress Reports

Keep records and logs of each task, and organize cumulative chronological

records for each major component, and for the complete system. Maintain a

continuous log for the UMCS. Keep complete logs and be available for

inspection on site, demonstrating that planned and systematic adjustments

and repairs have been accomplished for the UMCS.

3.9.8 Preventive Maintenance Requirements

**************************************************************************

NOTE: If the contractor will not be responsible for

Preventive Maintenance keep only the bracketed text

requiring a plan "detailing" preventive maintenance

SECTION 25 10 10 Page 95

(note this may include software maintenance as well

as hardware maintenance). Otherwise remove

"[detailing]" and keep the other bracketed text.

Delete the requirement for written requests to

reschedule maintenance if not required by the

project site.

**************************************************************************

[Perform maintenance procedures as described below, or more often if

required by the equipment manufacturer.] [Prepare a Preventive Maintenance

Work Plan as specified.]

3.9.8.1 Preventive Maintenance Work Plan

Prepare a Preventive Maintenance Work Plan [to schedule] [detailing] all

required preventive maintenance. Obtain Government approval of the Work

Plan as specified in paragraph PROJECT SEQUENCING.[ Strictly adhere to

the approved work plan to facilitate Government verification of work.][

If it is necessary to reschedule maintenance, make a written request to

the Government detailing the reasons for the proposed change at least five

days prior to the originally scheduled date. Scheduled dates will be

changed only with the prior written approval of the Government.]

[3.9.8.2 Semiannual Maintenance

**************************************************************************

NOTE: Coordinate with the project site to determine

whether or not to include the requirements for

Semiannual Maintenance. See also above notes

regarding maintenance of Government furnished

equipment and access requirements.

**************************************************************************

Perform the following Semiannual Maintenance as specified:

a. Perform data backups on all Server Hardware.

b. Run system diagnostics and correct diagnosed problems.

c. Perform fan checks and filter changes for UMCS hardware.

d. Perform all necessary adjustments on printers.

e. Resolve all outstanding problems.

f. Install new ribbons, ink cartridges and toner cartridges into

printers, and ensure that there is at least one spare ribbon or

cartridge located at each printer.

][3.9.8.3 Maintenance Procedures

**************************************************************************

NOTE: Coordinate with the project site to determine

whether or not to include the Maintenance Procedures

requirement (in whole or in part). See also above

notes regarding maintenance of Government furnished

equipment and access requirements.

SECTION 25 10 10 Page 96

Select whether notice must be given for maintenance

that will result in downtime (off-line) or for any

maintenance that MAY result in downtime. A

selection of 'will' is recommended unless the

project site requests otherwise.

Select appropriate down-times and notice times.

**************************************************************************

3.9.8.3.1 Maintenance Coordination

Coordinate any scheduled maintenance event that [will][may] result in

component downtime with the Government as follows, where time periods are

measured as actual elapsed time from beginning of equipment off-line

period, including working and non-working hours:

a. For non-redundant computer server hardware, provide [14] [_____] days

notice, components must be off-line for no more than [8] [_____] hours.

b. For non-redundant computer workstation hardware, provide [7] [_____]

days notice, components must be off-line for no more than [8] [_____]

hours.

c. for redundant computer server hardware, provide [7] [_____] days

notice, components must be off-line for no more than [36] [_____]

hours.

d. For redundant computer workstation hardware, provide [4] [_____] days

notice, components must be off-line for no more than [48] [_____]

hours.

e. For active (powered) control hardware, provide [14] [_____] days

notice, components must be off-line for no more than [6] [_____] hours.

f. For cabling and other passive network hardware, provide [21] [_____]

days notice, components must be off-line for no more than [12] [_____]

hours.

3.9.8.3.2 Software/Firmware

Software/firmware maintenance includes [____] [operating systems,

]application programs, and files required for the proper operation of the

UMCS regardless of storage medium. User (project site) developed software

is not covered by this contract, except that the UMCS software/firmware

must be maintained to allow user creation, modification, deletion, and

proper execution of such user-developed software as specified. Perform

diagnostics and corrective reprogramming as required to maintain total

UMCS operations as specified. Back up software before performing any

computer hardware and software maintenance. Do not modify any parameters

without approval from the Government. Properly document any approved

changes and additions, and update the appropriate manuals.

[3.9.8.3.3 Network

**************************************************************************

NOTE: Network maintenance should only be required

for Contractor furnished networks. If using a

Government furnished network delete the requirement.

**************************************************************************

SECTION 25 10 10 Page 97

Network maintenance includes testing transmission media and equipment to

verify signal levels, system data rates, errors and overall system

performance.

]]3.9.9 Service Call Reception

**************************************************************************

NOTE: Designer should coordinate with the project

site to determine if they want the Contractor to be

responsible for answering service calls only during

working hours or 24-7.

**************************************************************************

a. A Government representative will advise the Contractor by phone or in

person of all maintenance and service requests, as well as the

classification of each based on the definitions specified. A

description of the problem or requested work, date and time notified,

location, classification, and other appropriate information will be

placed on a Service Call Work Authorization Form by the Government.

b. Submit procedures for receiving and responding to service calls [24

hours per day, seven days a week, including weekends and holidays]

[during regular working hours]. Provide a single telephone number for

receipt of service calls during regular working hours; service calls

are to be considered received at the time and date the telephone call

is placed by the authorized Government representative.

c. Separately record each service call request, as received on the

Service Call Work Authorization form and complete the Service Call

Work Authorization form for each service call. Include the following

information in the completed form: the serial number identifying the

component involved, its location, date and time the call was received,

nature of trouble, names of the service personnel assigned to the

task, instructions describing what has to be done, the amount and

nature of the materials to be used, the time and date work started,

and the time and date of completion.

d. Respond to each service call request within [two] [_____] working

hours. Provide the status of any item of work within [four] [_____]

hours of the inquiry during regular working hours, and within [16]

[_____] hours after regular working hours or as needed to meet the

Equipment Repair requirements as specified.

3.9.10 Service Call Work Warranty

Provide a [1 year] [_____] unconditional warranty on service call work

which includes labor and material necessary to restore the equipment

involved in the initial service call to a fully operable condition. In

the event that service call work causes damage to additional equipment,

restore the system to full operation without cost to the Government.

Provide response times for service call warranty work equivalent to the

response times required by the initial service call.

3.9.11 System Modifications

Make recommendations for system modification in writing to the

Government. Do not make system modifications without prior approval of

the Government. Incorporate any modifications made to the system into the

SECTION 25 10 10 Page 98

Operations and Maintenance Instructions, and any other documentation

affected. Make available to the Government software updates for all

software furnished under this specification during the life of this

contract. Schedule at least one update near the end of the contract

period, at which time make available the latest released version of all

software provided under this specification, and install and validate it

upon approval by the Government.

3.10 TRAINING

**************************************************************************

NOTE: Training duration and content should be

modified to fit the requirements of the specific

job. For example, if this specification is to be

used to add to an existing UMCS or to replace a

portion of an existing UMCS the training

requirements should be relaxed.

**************************************************************************

Conduct training courses for designated personnel in the maintenance,

service, and operation of the system as specified, including specified

hardware and software. The training must be oriented to the specific

system provided under this contract. Provide audiovisual equipment and

other training material and supplies required for the training. When

training is conducted at Government facilities, the Government reserves

the right to record the training sessions for later use. A training day

is defined as 8 hours of classroom instruction, excluding lunchtime,

Monday through Friday, during the daytime shift in effect at the training

facility. For guidance in planning the required instruction, the

Contractor should assume that attendees will be tradesmen such as

electricians or boiler operators. Obtain approval of the training

schedule from the Government at least [30] [_____] days prior to the first

day of training.

3.10.1 Training Documentation

Prepare and submit one set of Training manuals for each of Basic Training

Documentation, Advanced Training Documentation, and Refresher Training

Documentation, where each set of documentation consists of:

3.10.1.1 Course Attendance List

Course Attendance List developed in coordination with and signed by the

[Controls] [HVAC] [Electrical] shop supervisor.

3.10.1.2 Training Manuals

Include an agenda, defined objectives for each lesson, and a detailed

description of the subject matter for each lesson in the training

manuals. Where portions of the course material are presented by

audiovisuals, include copies of those audiovisuals as a part of the

printed training manuals.

3.10.2 Basic Training

Conduct a Basic Training course at the project site on the installed

system for a period of no less than [5] [_____] training days during Phase

2 of the PVT. A maximum of [ten] [_____] personnel will attend this

course. Design training targeted towards training personnel in the

SECTION 25 10 10 Page 99

day-to-day operation and basic maintenance of the system. Upon completion

of this course, each student, using appropriate documentation, should be

able to start the system, operate the system, recover the system after a

failure, perform routine maintenance and describe the specific hardware

architecture and operation of the system. Include the following topics at

a minimum:

a. General system architecture.

b. Functional operation of the system, including workstations and system

navigation.

c. System start-up procedures.

d. Failure recovery procedures.

e. Schedule configuration.

f. Trend configuration.

g. Perform point overrides and override release.

h. Reports generation.

i. Alarm reporting and acknowledgements.

j. Diagnostics.

k. Historical files.

l. Maintenance procedures:

(1) Physical layout of each piece of hardware.

(2) Troubleshooting and diagnostic procedures.

(3) Preventive maintenance procedures and schedules.

3.10.3 Advanced Training

**************************************************************************

NOTE: This subpart uses tailoring options to

include requirements for selected protocols only.

1) CEA-709.1-D Network Configuration Tool is

included only when the LONWORKS tailoring option is

selected.

2) BACnet Network Browser is included only when the

BACNET tailoring option is selected.

3) Niagara Framework Engineering Tool is included

only when the NIAGARA FRAMEWORK tailoring option is

selected.

**************************************************************************

**************************************************************************

NOTE: Coordinate with the project site to select

the location of the Advanced Training (or leave it

up to the Contractor). Select the duration of the

training and the number of attendees.

**************************************************************************

SECTION 25 10 10 Page 100

Conduct an Advanced Operator Training course [at the project site]

[off-site or at the project site] for a period of not less then [five]

[_____] days. A maximum of [ten] [_____] personnel will attend this

course. Structure the course to consist of "hands-on" training under the

constant monitoring of the instructor. Include training on the M&C

Software, and the CEA-709.1-D Network Configuration Tool , and the BACnet

Network Browser, and the Niagara Framework Engineering Tool. Upon

completion of this course, the students should be fully proficient in the

operation and management of all system operations and must be able to

perform all tasks required to integrate a field control system into the

UMCS. Report the skill level of each student at the end of this course.

Include the following topics at a minimum:

a. A review of all topics in Basic Training

b. Using the CEA-709.1-D Network Configuration Tool for Network Management

and using the BACnet Network Browser for network discovery

c. M&C Software configuration, including but not limited to: creating and

editing system displays, alarms, schedules, trends, demand limiting

and calculations.

3.10.4 Refresher Training

**************************************************************************

NOTE: Refresher Training should be timed to take

place near the end of the 1-year warranty period.

If the UMCS is contracted out via an IDIQ process,

it may be desirable to repeat the Refresher Training

periodically.

**************************************************************************

Conduct a Refresher Training course at the project site for a period of

[two] [_____] training days when approved by the Government and as

specified in paragraph PROJECT SEQUENCING. A maximum of [ten] [_____]

personnel will attend the course. Structure the course to address

specific topics that the students need to discuss and to answer questions

concerning the operation of the system. Upon completion of the course,

the students should be fully proficient in system operation and have no

unanswered questions regarding operation of the installed UMCS. Correct

any system failures discovered during the Refresher Training at no cost to

the Government.

SECTION 25 10 10 Page 101

APPENDIX A

**************************************************************************

NOTE: The QC Checklist table may not display

properly in SpecsIntact. If it appears empty

right-click on the table and select "Make All Rows

Same Height" to make the entire table appear and

then adjust row heights as needed (such as reducing

row height for rows with less text).

**************************************************************************

QC CHECKLIST

This checklist is not all-inclusive of the requirements of this specification and

should not be interpreted as such.

This checklist is for (check one:)

Pre-Construction QC Checklist Submittal (Items 1-2) ( )

Post-Construction QC Checklist Submittal (Items 1-6) ( )

Close-out QC Checklist Submittal (Items 1-14) ( )

Instructions: Initial each item in the space provided (|____|) verifying that the

requirement has been met.

Verify the following items for Pre-Construction, Post-Construction and Closeout QC

Checklist Submittals:

1 Contractor Design Drawing Riser Diagram includes location and types

of all Control Hardware and Computer Hardware.

|____|

2 M&C Software supports the Niagara Framework, and ASHRAE 135, and

CEA-709.1-D, and MODBUS Protocol/MODBUS TCP/IP, and OPC DA. M&C

Software is BTL Listed as a B-AWS. M&C Software is LonWorks Network

Services (LNS) based.

|____|

Verify the following items for Post-Construction and Closeout QC Checklist Submittal:

SECTION 25 10 10 Page 102

QC CHECKLIST

3 Communication between the M&C Software and Niagara Framework field

control systems uses only Fox protocol.Communication between the M&C

Software and ASHRAE 135 field control systems uses only ASHRAE 135.

Communication between the M&C Software and CEA-709.1-D field control

systems uses only CEA-709.1-D. Communication between the M&C

Software and MODBUS Protocol/MODBUS TCP/IP field control systems

uses only MODBUS Protocol/MODBUS TCP/IP. Communication between the

M&C Software and OPC DA field control systems uses only OPC DA.

|____|

4 Connections to field control systems are via Niagara Framework

Supervisory Gateways.

[The following is NOT permitted when Niagara Framework is used and

therefore IS NOT PERMITTED for this project:

Connections to non-ASHRAE 135, non-CEA-709.1-D, non-Modbus, non-OPC

DA field control systems are via a Gateway from the field control

system to ASHRAE 135, or to CEA-709.1-D, or to Modbus, or to OPC DA,

or via a UMCS supported protocol without the use of a hardware

Gateway.]

|____|

5 Computer workstations and servers are installed as shown on the UMCS

Riser Diagram.

|____|

6 Training schedule and course attendee lists have been developed and

coordinated with shops and submitted.

|____|

Verify the following items for Closeout QC Checklists Submittal:

7 LNS Database is up-to-date and accurately represents the final

installed system. All points in field control systems have been

discovered using the Niagara Framework Engineering Tool and are

available at the M&C Software.

|____|

8 All software has been licensed to the Government. |____|

SECTION 25 10 10 Page 103

QC CHECKLIST

9 M&C software monitoring displays have been created for all building

systems, including all override and display points indicated on

Points Schedule drawings.

|____|

10 Final As-built Drawings accurately represent the final installed

system.

|____|

11 Default trends have been set up (per Points Schedule drawings). |____|

12 Scheduling has been configured at the M&C Software (per Occupancy

Schedule drawing).

|____|

13 O&M Instructions have been completed and submitted. |____|

14 Basic Operator and Advanced Training courses have been completed. |____|

___________________________________________ __________________

(QC Representative Signature) (Date)

-- End of Section --

SECTION 25 10 10 Page 104