Integration Ready Building Definition

Purpose:  This document defines the criteria for including buildings on the ARIMD “Integration Ready” list. All criteria listed under “Primary Requirements” must be met to be integrated to the EBCS server. The criteria listed as “Secondary Requirements” must be met for the system to achieve a high-level of functionality. The minimum standards that must be met for the secondary requirements is under the discretion of each Readiness Division.  All the criteria listed as “Critical” must be met to be included in the enterprise integration program. Any building considered “Integration Ready” may be considered for QUTM or UFERS funds for connection to the Enterprise Building Control System (EBCS).

Primary Requirements:

- Enduring; Not a list for demolition or for a major renovation, or real property disposal.

- The integration controller must be a JACE 8000 with a Niagara 4.7 license. It is permitted for the local BCS front-end (NAC) to also be the integration controller (IC JACE) if it meets the hardware and software license requirements. It is also permitted for an MDMS JACE to be the IC JACE if it meets the hardware and software license requirements.

Secondary Requirements:

- The existing control system was installed later than 2005.

  - Systems that were installed before 2005 maybe accepted on a building-by- building basis.

  - Both hardware and software product that are installed in the building are still supported by the manufacture or a local contractor

- A building level control system (BCS) installed in the building which controls on all major HVAC equipment. Major HVAC equipment that is typically connected to the BCS are, but not limited to:

  - Air handler units

  - Packaged or rooftop heating and cooling systems

  - Source of cooling for the building (e.g. chillers)

  - Source of heating for the building (e.g. boilers)

  - Zone/ Space/ Room temperature controls

  - Exhaust fans

- Optional equipment may be integrated into the BCS but are not necessary for enterprise integration.  Optional equipment that may also be integrated into the BCS are:

  - Lighting systems

  - Electric, Gas, and Water meters

  - Renewables

  - Emergency generation

- The BCS shall communicate in an open protocol that is common with current BCS standards. The two that are the most common for BCS’s are Building Automation and Control Networks (BACnet) and Local Operating Network (Lon Works).  Most control systems installed after 2005 utilize one of these communication protocols.

- The BCS needs to have the ability to be configured in a manner that will allow the enterprise integration controller to read and write to data points within the system.  This is a necessary requirement for the integration process.

- BCS points list with read and write points (analog inputs and analog outputs, digital/binary inputs and outputs, virtual inputs and outputs).  Should be the current point naming conventions.

  - Manufacture of the hardware in the BCS

  - Manufacture of the software in the BCS

  - Current version of software that is installed in the BCS

  - Last software update

- Submittals for control drawing with sequence of operation

  - Administrative level or highest level in the BCS username and password.

- Floorplans of the building for the purpose of building graphics of the building layout.

- Point of contact for the local contactor that supports the controls at the BCS level