## Instructions
SRA: Site Readiness Assessment
Site Readiness Assessment Instructions
The Site Readiness Assessment (SRA) workbook is a tool used to help guide informed decisions in regards to Army Reserve Enterprise Building Control System (EBCS) integration. This tool will capture basic facility information, information regarding the HVAC equipment and level of functionality, and information regarding the existing BCS and local network infrastructure.
This tool will also assist with defining the integration readiness status of the facility. The readiness will be categorized as either "Ready", "Not Ready", or "Partially Ready".
Defining the preliminary costs is critical to the SRA process. Preliminary costs must be established for each section and a recommended integration strategy is required on the Output tab. See the Preliminary Costs instructions below for further guidance.
This workbook is intended to be used for a single facility. Additional workbooks must be used for additional facilities.
This SRA workbook will be used to generate some of the information needed for the SRA report. The workbook will then be delivered to responsible POCs with the SRA report as part of an SRA package.
SRA List of Acronyms
AR - Army Reserve |  |  |  | LON - communications protocol (LonWorks, est. by Echelon Co.)
ARNET - Army Reserve Network |  |  |  | MDMS - Meter Data Management System
BACNET - communications protocol (Building Automation and Control (BAC) networks) |  |  |  | NAC - Network Area Controller
BCS - Building Control System |  |  |  | NEMA - National Electrical Manufactures Association
CO2 - Carbon Dioxide |  |  |  | RD - Readiness Division
EBCS - Enterprise Building Control System |  |  |  | RPI - Real Property Index
FACID - Facility Identification (XX###) |  |  |  | SQFT - Square Feet
HVAC - Heating, Ventilation, and Air Conditioning |  |  |  | SRA - Site Readiness Assessment
IP - Internet Protocol |  |  |  | VAC - Volts, AC Power
IT - Information Technology |  |  |  | VFD - Variable Frequency Drive
Functional Test
The functional test is performed on each piece of HVAC equipment on the BCS, where sensor outputs and control capabilities are graded with a Pass/Fail approach. The equipment can be validated by altering minor setpoints in the system and observing the change in temperature and flow rates as appropriate. Physical validation is also recommended while onsite, and can be performed on all major pieces of equipment and sampling minor pieces of equipment. The result of the functionality test provides a summary of the system's health by calculating the percentage of data points that passed the test.
Below are the categorical guidelines for the functional test. Any categories reporting FAIL must be further explained in the "Notes" section for the corresponding line.
Temperature and Pressure Sensors:
1 | Confirm the temperature and pressure sensors are accurately calibrated
Damper Positions:
1 | Confirm the damper actuators are accurately calibrated
2 | Verify the dampers can be commanded by the user on the BCS
Fan/Pump Control
1 | Confirm the fans/pumps are operating as stated in the BCS
2 | Verify the fans/pumps can be commanded by the user on the BCS
3 | Note if the fans/pumps have VFDs
Enable/Disable
1 | Verify the equipment can be enabled/disabled by the user on the BCS
2 | Verify the enable/disable temperature setpoints for the heating and cooling loops can be commanded by the user on the BCS
Heating Control & Cooling Control
1 | Verify the supply temperature setpoints for the heating/cooling loops can be edited by the user on the BCS
2 | Verify the hot/chilled water valves on AHUs can be edited by the user on the BCS
3 | Verify the zone temperature setpoints can be edited by the user on the BCS
Economizer Control
1 | Verify the dampers can be commanded by the user on the BCS
2 | Verify the economize setpoint can be edited by the user on the BCS
Humidity and CO2 Sensors
1 | Confirm the humidity and CO2 sensors are accurately calibrated
Multi-Gas Sensors
1 | Comment in the notes which type of gas is being monitored (CO, NO, etc.)
2 | Confirm the gas sensors are accurately calibrated
Occupancy Sensors
1 | Confirm the occupancy sensors are functional
Communication Status
1 | Confirm the equipment is communicating to the BCS (not offline)
O&M Deficiency
1 | List any detailed O&M deficiency associated with the equipment. See next section for details.
O&M Examples
This section lists examples of common O&M deficiencies. This list is not comprehensive. It is primarily meant as a guide to help users document the appropriate amount of information for O&M deficiencies.
For example, instead of documenting "fan fail", it is critical to document how or why the fan has failed since it could be attributed to any (but not limited to) of the following:
VFD Issues:
Manually configured to HAND at VFD keypad
Turned off / disconnected
Offline
Air Supply:
Duct leaks or blockages
Dirty filters
Duct static station fail
Fan:
Worn bearings
Worn belt
Manually on / off
BCS:
Offline controller
Failed status sensor
Equipment doesn't respond to commands
O&M List
This section is dedicated to listing all of the O&M and BCS deficencies observed during the SRA.
Integration Ready Definition
This section defines the criteria for including buildings on the ARIMD “Integration Ready” list. A fully integration-ready system meets the “Fully Integration-Ready Requirements” listed in tab "Integration Ready Definition" and can be integrated to EBCS as-is. A potential integration ready candidate meets, at minimum, the “Potential Integration Ready Candidates’ Requirements”. Systems that are classified as partially integration ready candidates are systems that can be integrated to EBCS by adding a qualified integration controller and/or being upgraded to full integration ready status. Systems that appear to be integration ready, but do not follow the EBCS graphics and point name standards are also considered as partially ready. Systems that do not meet either fully integration ready requirements or are partially integration ready candidates are deemed as not integration ready. Systems that are not integration ready may require significant upgrades to the HVAC and/or BCS to enable integration. The strategy for these systems is decided by ARIMD and each RD on a building-by-building basis. The criteria listed as “Functionality Considerations” must be met for the system to achieve a high-level of functionality. The minimum standards that must be met for the functional considerations are under the discretion of each Readiness Division.
Integration Ready Definition
This section defines the criteria for including buildings on the ARIMD “Integration Ready” list. A fully integration-ready system meets the “Fully Integration-Ready Requirements” listed in tab "Integration Ready Definition" and can be integrated to EBCS as-is. A potential integration ready candidate meets, at minimum, the “Potential Integration Ready Candidates’ Requirements”. Systems that are classified as partially integration ready candidates are systems that can be integrated to EBCS by adding a qualified integration controller and/or being upgraded to full integration ready status. Systems that appear to be integration ready, but do not follow the EBCS graphics and point name standards are also considered as partially ready. Systems that do not meet either fully integration ready requirements or are partially integration ready candidates are deemed as not integration ready. Systems that are not integration ready may require significant upgrades to the HVAC and/or BCS to enable integration. The strategy for these systems is decided by ARIMD and each RD on a building-by-building basis. The criteria listed as “Functionality Considerations” must be met for the system to achieve a high-level of functionality. The minimum standards that must be met for the functional considerations are under the discretion of each Readiness Division.
Integration Ready Status
This section provides the critical criteria for the BCS to determine the integration ready status of the system.
If the system is "Integration Ready", it meets all criteria listed and can be integrated as-is to EBCS.
If the system is "Partially Integration Ready", it partially meets the criteria for integration and may or may not be able to be integrated into EBCS as-is. For example, a system that meets the integration criteria
expect for the graphics and point naming conventions are determined to be "Partially Integration Ready" because costs of integration will be higher than systems that are truly integration ready and do not need
graphics or point names converted.
Level of Completeness
Level of completeness will be determined by the SRA team while onsite by providing a ranking of "Low", "Med", "High". The intent of this metric is to identify major pieces of HVAC equipment that are missing from
the BCS.
Onsite Checklist
All information outlined about the building, hardware, and HVAC must be filled out.
Utility Meters and MDMS
All information outlined about the utility meters and MDMS Jace (if applicable) must be filled out.
MDMS Jace may qualify to be used as an EBCS Jace. If the MDMS Jace will not be used as an EBCS Jace, then the goal is to integrate the utility meters directly to the local BCS/NAC or EBCS Jace to avoid a double-Jace configuration.
Alternatively, the MDMS Jace may be integrated to the EBCS Jace if technical or physical limitation prevent the utility meters from being directly integrated to the EBCS Jace. Justification for this method must be provided.
Preliminary Costs
The preliminary costs for EBCS integration must be calculated to assist the Readiness Division (RD) in determining which EBCS integration strategies are most appropriate for each system.
Integration costs are any costs associated with Part C: EBCS Integration Costs. These are costs needed to integrate the system to EBCS.
Non-integration costs are any costs associated with Part A and/or Part D. These are costs needed to enable integration and/or costs to improve the functionality of the system. This DOES NOT include costs to integrate the system to the EBCS.
The preliminary costs are broken into three main categories:
| Part A: | Costs for enabling EBCS Integration. These are the costs are associated with preparing the EBCS Jace for integration based on integration ready status of the building.
|  | Option 1: | Using NAC as an EBCS JACE
|  | Option 2: | Install an EBCS JACE
|  | Option 3: Replacing local BCS front-end with Jace 8000 for buildings deemed as "Not Integration Ready" or "Potential Integration Ready" to use qualified JACE as IC | Replacing local BCS front-end with Jace 8200
|  | Option 4: | Use MDMS Jace as EBCS Jace
| Part B: | Costs for utility meter integration. The priority option is Option 1 to help avoid multi-Jace configurations.
|  | Option 1: | Integrating utility meters directly to EBCS Jace
|  | Option 2: | Integrating MDMS Jace to the EBCS Jace.
| Part C: | EBCS Integration Cost. These are costs associated with integrating EBCS to EBCS
| Part D: | Costs for Improving Functionality & Completeness. These costs will increase the level of functionality with the system.
Outputs
Summary Tables
--- | Integration Ready: Displays the system's integration ready status.
--- | Level of Functionality: Displays the system's current level of functionality as definied by the SRA team.
--- | Level of Completeness: Displays the system's current level of completeness as definied by the SRA team.
--- | Preliminary Costs: Summary of costs for achieving EBCS integration, bringing systems to integration ready status, and costs for improving functionality. Recommended strategies and final preliminary costs are required as inputs in this table.
--- | Site Information: Basic site and building information
--- | System Health: Calculated by the number of "Pass" vs "Fail" selections from the Functional Test.
--- | BCS / NAC Information: Information regarding the existing BCS / NAC
--- | Functional Test: Copy of the Functional Test
These output tables may be used to generate some of the information needed for the SRA report. The workbook will then be delivered to responsible POCs with the SRA report as part of an SRA package.

## Functional Test
Equipment Name | Equipment Type | Temperature Sensors | Pressure Sensors | Damper Positions | Fan/Pump Control | Enable / Disable | Heating Control | Cooling Control | Economizer Control | Humidity Sensor | CO2 Sensors | Multi-Gas Sensors | Occupancy Sensors | Communication Status | O&M Deficiency | Notes

## Data Tables (hidden)
[10 empty] | AI | BI | AO | BO | NVR | NVW
[8 empty] | AHU HW/CW | 32 | 10 | 5 | 3 | 2 | 3 | 9
AHU HW/CW
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Mixed Air Temperature | MA-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Warmer Cooler Adjust | WC-ADJ | X
Return CO2 | CO2 | X
Supply Airflow | SPLY-AIR-FLOW | X
Return Airflow | RTN-AIR-FLOW | X
Outside Airflow | EX-AIR-FLOW | X
Temporary Occupancy Button | TEMP-OCC |  | X
Supply Fan Status | SF-S |  | X
Return Fan Status | RF-S |  | X
Low Temperature Alarm | LA-T |  | X
Filter Alarm | FLT-ALM |  | X
Economizer Damper Output | ECON-DAMP-O |  |  | X
Heating Valve Output | HTG-VAL-O |  |  | X
Cooling Valve Output | CLG-VAL-O |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Return Fan Command | RF-C |  |  |  | X
Discharge Air Setpoint | DA-SP |  |  |  |  | X
Cooling Command | [5 empty] | X
Heating Command | [5 empty] | X
Economizer Change Over Setpoint | ECON-CHOV-SP | [5 empty] | X
Minimum Outside Air Position | [6 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | AHU HW/DX | 37 | 10 | 5 | 3 | 2 | 4 | 13
AHU HW/DX
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Mixed Air Temperature | MA-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Warmer Cooler Adjust | WC-ADJ | X
Return CO2 | CO2 | X
Supply Airflow | SPLY-AIR-FLOW | X
Return Airflow | RTN-AIR-FLOW | X
Outside Airflow | EX-AIR-FLOW | X
Temporary Occupancy Button | TEMP-OCC |  | X
Supply Fan Status | SF-S |  | X
Return Fan Status | RF-S |  | X
Low Temperature Alarm | LA-T |  | X
Filter Alarm | FLT-ALM |  | X
Economizer Damper Output | ECON-DAMP-O |  |  | X
Heating Valve Output | HTG-VAL-O |  |  | X
Cooling Stage Output | CLG-STG-O |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Return Fan Command | RF-C |  |  |  | X
Effective Discharge Air Setpoint | [5 empty] | X
Cooling Command | [5 empty] | X
Heating Command | [5 empty] | X
Max or Average Damper position | [5 empty] | X
Economizer Change Over Setpoint | ECON-CHOV-SP | [5 empty] | X
Minimum Outside Air Position | [6 empty] | X
Discharge Air Setpoint | DA-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Discharge air setpoint Low | [6 empty] | X
Discharge air setpoint High | [6 empty] | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | AHU HW Only | 34 | 11 | 7 | 4 | 2 | 3 | 7
AHU HW Only
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Mixed Air Temperature | MA-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Duct Static Pressure |  | X
Return CO2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Supply Airflow | SPLY-AIR-FLOW | X
Return Airflow | RTN-AIR-FLOW | X
Outside Airflow | EX-AIR-FLOW | X
Temporary Occupancy Button | TEMP-OCC |  | X
Supply Fan Status | SF-S |  | X
Supply Fan Alarm | SF-ALM |  | X
Return Fan Status | RF-S |  | X
Return Fan Alarm | RF-ALM |  | X
Low Temperature Alarm | LA-T |  | X
Filter Alarm | FLT-ALM |  | X
Economizer Damper Output | ECON-DAMP-O |  |  | X
Supply Fan Output | SF-O |  |  | X
Return Fan Output | RF-O |  |  | X
Heating Valve Output | HTG-VAL-O |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Return Fan Command | RF-C |  |  |  | X
Heating Command | [5 empty] | X
Effective Zone Temperature Setpoint | [5 empty] | X
Max or Average Damper position | [5 empty] | X
Economizer Change Over Setpoint | ECON-CHOV-SP | [5 empty] | X
Minimum Outside Air Position | [6 empty] | X
Discharge Air Setpoint | DA-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Zone Temperature Setpoint Low | [6 empty] | X
Zone Temperature Setpoint High | [6 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | AHU VAV Cooling only | 35 | 10 | 6 | 4 | 2 | 5 | 8
AHU VAV Cooling only
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Mixed Air Temperature | MA-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Duct Static Pressure |  | X
Return/Zone Co2 | CO2 | X
Supply Airflow | SPLY-AIR-FLOW | X
Return Airflow | RTN-AIR-FLOW | X
Outside Airflow | EX-AIR-FLOW | X
Supply Fan Status | SF-S |  | X
Supply Fan Alarm | SF-ALM |  | X
Return Fan Status | RF-S |  | X
Return Fan Alarm | RF-ALM |  | X
Low Temperature Alarm | LA-T |  | X
Filter Alarm | FLT-ALM |  | X
Economizer Damper Output | ECON-DAMP-O |  |  | X
Supply Fan Output | SF-O |  |  | X
Return Fan Output | RF-O |  |  | X
Cooling Valve Output | CLG-VAL-O |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Return Fan Command | RF-C |  |  |  | X
Discharge Air Setpoint | DA-SP |  |  |  |  | X
Effective Discharge Air Setpoint | [5 empty] | X
Cooling Command | [5 empty] | X
Effective Discharge Air Setpoint | [5 empty] | X
Max or Average Damper position | [5 empty] | X
Economizer Change Over Setpoint | ECON-CHOV-SP | [5 empty] | X
Minimum Outside Air Position | [6 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Discharge air setpoint Low | [6 empty] | X
Discharge air setpoint High | [6 empty] | X
Duct Static Setpoint Low | [6 empty] | X
Duct Static Setpoint High | [6 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | AHU VAV with Heat | 33 | 10 | 6 | 4 | 2 | 3 | 8
AHU VAV with Heat
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Mixed Air Temperature | MA-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Duct Static Pressure |  | X
Return/Zone Co2 | CO2 | X
Supply Airflow | SPLY-AIR-FLOW | X
Return Airflow | RTN-AIR-FLOW | X
Outside Airflow | EX-AIR-FLOW | X
Supply Fan Status | SF-S |  | X
Supply Fan Alarm | SF-ALM |  | X
Return Fan Status | RF-S |  | X
Return Fan Alarm | RF-ALM |  | X
Low Temperature Alarm | LA-T |  | X
Filter Alarm | FLT-ALM |  | X
Economizer Damper Output | ECON-DAMP-O |  |  | X
Supply Fan Output | SF-O |  |  | X
Return Fan Output | RF-O |  |  | X
Heating Valve Output | HTG-VAL-O |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Return Fan Command | RF-C |  |  |  | X
Discharge Air Setpoint | DA-SP |  |  |  |  | X
Heating Command | [5 empty] | X
Max or Average Damper position | [5 empty] | X
Economizer Change Over Setpoint | ECON-CHOV-SP | [5 empty] | X
Minimum Outside Air Position | [6 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Discharge air setpoint Low | [6 empty] | X
Discharge air setpoint High | [6 empty] | X
Duct Static Setpoint Low | [6 empty] | X
Duct Static Setpoint High | [6 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | AHU Duel Duct | 33 | 10 | 4 | 3 | 2 | 4 | 10
AHU Duel Duct
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Mixed Air Temperature | MA-T | X
Return Air Temperature | RA-T | X
Hot Deck Temperature | HD-T | X
Cold Deck Temperature | CD-T | X
Return/Zone Co2 | CO2 | X
Supply Airflow | SPLY-AIR-FLOW | X
Return Airflow | RTN-AIR-FLOW | X
Outside Airflow | EX-AIR-FLOW | X
Supply Fan Status | SF-S |  | X
Return Fan Status | RF-S |  | X
Low Temperature Alarm | LA-T |  | X
Filter Alarm | FLT-ALM |  | X
Economizer Damper Output | ECON-DAMP-O |  |  | X
Heating Valve Output | HTG-VAL-O |  |  | X
Cooling Valve Output | CLG-VAL-O |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Return Fan Command | RF-C |  |  |  | X
Discharge Air Setpoint | DA-SP |  |  |  |  | X
Max or Average Cooling Command | [5 empty] | X
Max or Average Heating Command | [5 empty] | X
Max or Average Damper position | [5 empty] | X
Hot Deck setpoint Low | [6 empty] | X
Hot Deck setpoint High | [6 empty] | X
Outside Air Setpoint Low | [6 empty] | X
Outside Air Setpoint High | [6 empty] | X
Unoccupied Hot Deck Setpoint | [6 empty] | X
Economizer Change Over Setpoint | ECON-CHOV-SP | [5 empty] | X
Minimum Outside Air Position | [6 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | MAU with Heat/Cool | 20 | 4 | 4 | 2 | 2 | 1 | 7
MAU with Heat/Cool
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Discharge Air Temperature | DA-T | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Supply Fan Status | SF-S |  | X
Supply Fan Alarm | SF-ALM |  | X
Low Temperature Alarm | LA-T |  | X
Supply Fan Output | SF-O |  |  | X
Heating Valve Output | HTG-VAL-O |  |  | X
Heating Command | HTG-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Discharge Air Setpoint | DA-SP |  |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | MAU with Heat/Cool | 20 | 4 | 4 | 2 | 2 | 1 | 7
MAU with Heat/Cool
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Discharge Air Temperature | DA-T | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Supply Fan Status | SF-S |  | X
Supply Fan Alarm | SF-ALM |  | X
Low Temperature Alarm | LA-T |  | X
Supply Fan Output | SF-O |  |  | X
Heating Valve Output | HTG-VAL-O |  |  | X
Heating Command | HTG-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Discharge Air Setpoint | DA-SP |  |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Energy Recovery Unit | 18 | 6 | 4 | 4 | 3 | 0 | 1
Energy Recovery Unit
Description | NAME | AI | BI | AO | BO | NVR | NVW
Entering Outside Air Temperature | ENT-OA-T | X
Entering Exhaust Air Temperature | ENT- EXH-T | X
Leaving Exhaust Air Temperature | LEA-EXH-T | X
Leaving Outside Air Temperature | LEA-OA-T | X
Supply Airflow |  | X
Exhaust Airflow |  | X
Supply Filter Alarm | SPLY-FLT-ALM |  | X
Exhaust Filter Alarm | EX-FLT-ALM |  | X
Supply Fan Status | SF-S |  | X
Exhaust Fan Status | EF-S |  | X
Supply Fan Output | SF-O |  |  | X
Exhaust Fan Output | EF-O |  |  | X
Bypass Damper Command | BYP-DAMP-C |  |  | X
Heating Valve Output | HTG-VLV-O |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Exhaust Fan Command | EXH-C |  |  |  | X
Heat Wheel Command | HT-WHL-C |  |  |  | X
Discharge Air Temperature Setpoint | DA-T | [5 empty] | X
[8 empty] | Gas Furnace | 13 | 4 | 1 | 0 | 3 | 0 | 5
Gas Furnace
Description | NAME | AI | BI | AO | BO | NVR | NVW
Zone Temperature | ZN-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Heating Stage 1 Command | HTG-1-C |  |  |  | X
Heating Stage 2 Command | HTG-2-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Electric Furnace | 13 | 4 | 1 | 0 | 3 | 0 | 5
Electric Furnace
Description | NAME | AI | BI | AO | BO | NVR | NVW
Zone Temperature | ZN-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Heating Stage 1 Command | HTG-1-C |  |  |  | X
Heating Stage 2 Command | HTG-2-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Split System AC/Elec Heat | 18 | 5 | 1 | 0 | 4 | 8
Split System AC/Elec Heat
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Heating Stage 1 Command | HTG-1-C |  |  |  | X
Heating Stage 2 Command | HTG-2-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Cooling Stage 1 Command | CLG-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Split System AC/Gas Heat | 17 | 5 | 1 | 0 | 3 | 0 | 8
Split System AC/Gas Heat
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Heating Stage 1 Command | HTG-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Cooling Stage 1 Command | CLG-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Water Source HP | 13 | 2 | 1 | 0 | 6 | 0 | 4
Water Source HP
Description | NAME | AI | BI | AO | BO | NVR | NVW
Zone Temperature | ZN-T | X
Supply Air Temperature | SA-T | X
Supply Fan Status | SF-S |  | X
Occupancy Command | OCC-C |  |  |  | X
Reversing Valve Command | REV-C |  |  |  | X
Auxiliary Heating Command | AUX-HTG-C |  |  |  | X
1st Stage Compressor Command | COMP1-C |  |  |  | X
2nd Stage Compressor Command | COMP2-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
[8 empty] | RTU Eccon 1 Cool/Elc | 20 | 7 | 1 | 1 | 3 | 0 | 8
RTU Eccon 1 Cool/Elc
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Mixed Air Temperature | MA-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Economizer Damper Output | ECON-DAMP-O |  |  | X
Heating Stage 1 Command | HTG-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Cooling Stage 1 Command | CLG-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | RTU Eccon 2 Cool/Elc | 22 | 7 | 1 | 1 | 5 | 0 | 8
RTU Eccon 2 Cool/Elc
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Mixed Air Temperature | MA-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Economizer Damper Output | ECON-DAMP-O |  |  | X
Heating Stage 1 Command | HTG1-C |  |  |  | X
Heating Stage 2 Command | HTG2-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Cooling Stage 1 Command | CLG1-C |  |  |  | X
Cooling Stage 2 Command | CLG2-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | RTU Eccon 1 Cool/Gas | 20 | 7 | 1 | 1 | 3 | 0 | 8
RTU Eccon 1 Cool/Gas
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Mixed Air Temperature | MA-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Economizer Damper Output | ECON-DAMP-O |  |  | X
Heating Stage 1 Command | HTG-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Cooling Stage 1 Command | CLG-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | RTU Eccon 1 Cool/Gas Mod | 21 | 7 | 1 | 2 | 3 | 0 | 8
RTU Eccon 1 Cool/Gas Mod
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Mixed Air Temperature | MA-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Economizer Damper Output | ECON-DAMP-O |  |  | X
Modulating Gas Burner | HTG-Mod |  |  | X
Heating Stage 1 Command | HTG-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Cooling Stage 1 Command | CLG-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | RTU Eccon 2 Cool/Gas | 21 | 7 | 1 | 1 | 4 | 0 | 8
RTU Eccon 2 Cool/Gas
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Mixed Air Temperature | MA-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Economizer Damper Output | ECON-DAMP-O |  |  | X
Heating Stage 1 Command | HTG-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Cooling Stage 1 Command | CLG1-C |  |  |  | X
Cooling Stage 2 Command | CLG2-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | RTU Eccon 2 Cool/Gas Mod | 22 | 7 | 1 | 2 | 4 | 0 | 8
RTU Eccon 2 Cool/Gas Mod
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Mixed Air Temperature | MA-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Economizer Damper Output | ECON-DAMP-O |  |  | X
Modulating Gas Burner | HTG-Mod |  |  | X
Heating Stage 1 Command | HTG-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Cooling Stage 1 Command | CLG1-C |  |  |  | X
Cooling Stage 2 Command | CLG2-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | RTU 1 Cool/Elc | 18 | 6 | 1 | 0 | 3 | 0 | 8
RTU 1 Cool/Elc
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Heating Stage 1 Command | HTG-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Cooling Stage 1 Command | CLG-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | RTU 2 Cool/Elc | 20 | 6 | 1 | 0 | 5 | 0 | 8
RTU 2 Cool/Elc
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Heating Stage 1 Command | HTG1-C |  |  |  | X
Heating Stage 2 Command | HTG2-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Cooling Stage 1 Command | CLG1-C |  |  |  | X
Cooling Stage 2 Command | CLG2-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | RTU 1 Cool/Gas | 18 | 6 | 1 | 0 | 3 | 8
RTU 1 Cool/Gas
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Heating Stage 1 Command | HTG-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Cooling Stage 1 Command | CLG-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | RTU 1 Cool/Gas Mod | 19 | 6 | 1 | 1 | 3 | 0 | 8
RTU 1 Cool/Gas Mod
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Modulating Gas Burner | HTG-Mod |  |  | X
Heating Stage 1 Command | HTG-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Cooling Stage 1 Command | CLG-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | RTU 2 Cool/Gas Mod | 19 | 6 | 1 | 0 | 4 | 0 | 8
RTU 2 Cool/Gas Mod
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Heating Stage 1 Command | HTG-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Cooling Stage 1 Command | CLG1-C |  |  |  | X
Cooling Stage 2 Command | CLG2-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | RTU 2 Cool/Gas Mod | 20 | 6 | 1 | 1 | 4 | 0 | 8
RTU 2 Cool/Gas Mod
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Zone Temperature | ZN-T | X
Return Air Temperature | RA-T | X
Discharge Air Temperature | DA-T | X
Return/Zone Co2 | CO2 | X
Warmer Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | TEMP-OCC |  | X
Modulating Gas Burner | HTG-Mod |  |  | X
Heating Stage 1 Command | HTG-C |  |  |  | X
Supply Fan Command | SF-C |  |  |  | X
Cooling Stage 1 Command | CLG1-C |  |  |  | X
Cooling Stage 2 Command | CLG2-C |  |  |  | X
Zone Temperature Setpoint | ZN-SP | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Zone DA-T Control | 15 | 3 | 1 | 1 | 0 | 1 | 9
Zone DA-T Control
Description | NAME | AI | BI | AO | BO | NVR | NVW
Zone Temperature | ZN-T | X
Discharge Air Temperature | DA-T | X
Warmer/Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | OCC-OVRID |  | X
Damper Command | DAMP-O |  |  | X
Effective Discharge Air Setpoint | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Effective Zone Setpoint | EFF-ZN-SP | [5 empty] | X
Zone Temperature Deadband | [6 empty] | X
Discharge air setpoint Low | [6 empty] | X
Discharge air setpoint High | [6 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Zone Room Control | 11 | 3 | 1 | 1 | 0 | 1 | 5
Zone Room Control
Description | NAME | AI | BI | AO | BO | NVR | NVW
Zone Temperature | ZN-T | X
Discharge Air Temperature | DA-T | X
Warmer/Cooler Adjust | WC-ADJ | X
Temporary Occupancy Button | OCC-OVRID |  | X
Damper Command | DAMP-O |  |  | X
Effective Zone Setpoint | EFF-ZN-SP |  |  |  |  | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | VAV No Fan/No Reheat | 27 | 5 | 1 | 1 | 0 | 2 | 18
VAV No Fan/No Reheat
Description | NAME | AI | BI | AO | BO | NVR | NVW
Flow Ring Diff Pressure |  | X
Zone Temperature |  | X
Discharge Air Temperature |  | X
Warmer/Cooler Adjust |  | X
CO2 Sensor |  | X
Temporary Occupancy Button |  |  | X
Damper Output |  |  |  | X
Cooling Command | [5 empty] | X
System Mode | [5 empty] | X
Supply Air Temperature | [6 empty] | X
Zone Temperature Setpoint | [6 empty] | X
Zone Setpoint Bias | [6 empty] | X
Occupied Cooling Setpoint | [6 empty] | X
Unoccupied Cooling Setpoint | [6 empty] | X
Occupied Heating Setpoint | [6 empty] | X
Unoccupied Heating Setpoint | [6 empty] | X
Cooling Outside Air Lockout | [6 empty] | X
Supply Airflow Setpoint | [6 empty] | X
Cooling Maximum Flow | [6 empty] | X
Cooling Minimum Flow | [6 empty] | X
Cooling Unoccupied Flow | [6 empty] | X
Heat Maximum Flow | [6 empty] | X
Heating Minimum Flow | [6 empty] | X
Heating Unoccupied Flow | [6 empty] | X
Cool Down Minimum Flow | [6 empty] | X
Warm Up Minimum Flow | [6 empty] | X
Occupancy Command | [6 empty] | X
[8 empty] | VAV Reheat/Water | 28 | 5 | 1 | 2 | 0 | 2 | 18
VAV Reheat/Water
Description | NAME | AI | BI | AO | BO | NVR | NVW
Flow Ring Diff Pressure |  | X
Zone Temperature |  | X
Discharge Air Temperature |  | X
Warmer/Cooler Adjust |  | X
CO2 Sensor |  | X
Temporary Occupancy Button |  |  | X
Damper Output |  |  |  | X
Heating Valve |  |  |  | X
Cooling Command | [5 empty] | X
System Mode | [5 empty] | X
Supply Air Temperature | [6 empty] | X
Zone Temperature Setpoint | [6 empty] | X
Zone Setpoint Bias | [6 empty] | X
Occupied Cooling Setpoint | [6 empty] | X
Unoccupied Cooling Setpoint | [6 empty] | X
Occupied Heating Setpoint | [6 empty] | X
Unoccupied Heating Setpoint | [6 empty] | X
Cooling Outside Air Lockout | [6 empty] | X
Supply Airflow Setpoint | [6 empty] | X
Cooling Maximum Flow | [6 empty] | X
Cooling Minimum Flow | [6 empty] | X
Cooling Unoccupied Flow | [6 empty] | X
Heat Maximum Flow | [6 empty] | X
Heating Minimum Flow | [6 empty] | X
Heating Unoccupied Flow | [6 empty] | X
Cool Down Minimum Flow | [6 empty] | X
Warm Up Minimum Flow | [6 empty] | X
Occupancy Command | [6 empty] | X
[8 empty] | VAV Reheat/Elec | 28 | 5 | 1 | 1 | 1 | 2 | 18
VAV Reheat/Elec
Description | NAME | AI | BI | AO | BO | NVR | NVW
Flow Ring Diff Pressure |  | X
Zone Temperature |  | X
Discharge Air Temperature |  | X
Warmer/Cooler Adjust |  | X
CO2 Sensor |  | X
Temporary Occupancy Button |  |  | X
Damper Output |  |  |  | X
Heating Command |  |  |  |  | X
Cooling Command | [5 empty] | X
System Mode | [5 empty] | X
Supply Air Temperature | [6 empty] | X
Zone Temperature Setpoint | [6 empty] | X
Zone Setpoint Bias | [6 empty] | X
Occupied Cooling Setpoint | [6 empty] | X
Unoccupied Cooling Setpoint | [6 empty] | X
Occupied Heating Setpoint | [6 empty] | X
Unoccupied Heating Setpoint | [6 empty] | X
Cooling Outside Air Lockout | [6 empty] | X
Supply Airflow Setpoint | [6 empty] | X
Cooling Maximum Flow | [6 empty] | X
Cooling Minimum Flow | [6 empty] | X
Cooling Unoccupied Flow | [6 empty] | X
Heat Maximum Flow | [6 empty] | X
Heating Minimum Flow | [6 empty] | X
Heating Unoccupied Flow | [6 empty] | X
Cool Down Minimum Flow | [6 empty] | X
Warm Up Minimum Flow | [6 empty] | X
Occupancy Command | [6 empty] | X
[8 empty] | VAV Fan Pow/Water | 30 | 5 | 2 | 3 | 0 | 2 | 18
VAV Fan Pow/Water
Description | NAME | AI | BI | AO | BO | NVR | NVW
Flow Ring Diff Pressure |  | X
Zone Temperature |  | X
Discharge Air Temperature |  | X
Warmer/Cooler Adjust |  | X
CO2 Sensor |  | X
Temporary Occupancy Button |  |  | X
Fan Status |  |  | X
Fan Command |  |  |  | X
Damper Output |  |  |  | X
Heating Valve |  |  |  | X
Cooling Command | [5 empty] | X
System Mode | [5 empty] | X
Supply Air Temperature | [6 empty] | X
Zone Temperature Setpoint | [6 empty] | X
Zone Setpoint Bias | [6 empty] | X
Occupied Cooling Setpoint | [6 empty] | X
Unoccupied Cooling Setpoint | [6 empty] | X
Occupied Heating Setpoint | [6 empty] | X
Unoccupied Heating Setpoint | [6 empty] | X
Cooling Outside Air Lockout | [6 empty] | X
Supply Airflow Setpoint | [6 empty] | X
Cooling Maximum Flow | [6 empty] | X
Cooling Minimum Flow | [6 empty] | X
Cooling Unoccupied Flow | [6 empty] | X
Heat Maximum Flow | [6 empty] | X
Heating Minimum Flow | [6 empty] | X
Heating Unoccupied Flow | [6 empty] | X
Cool Down Minimum Flow | [6 empty] | X
Warm Up Minimum Flow | [6 empty] | X
Occupancy Command | [6 empty] | X
[8 empty] | VAV Fan Pow/Elec. | 30 | 5 | 2 | 2 | 1 | 2 | 18
VAV Fan Pow/Elec.
Description | NAME | AI | BI | AO | BO | NVR | NVW
Flow Ring Diff Pressure |  | X
Zone Temperature |  | X
Discharge Air Temperature |  | X
Warmer/Cooler Adjust |  | X
CO2 Sensor |  | X
Temporary Occupancy Button |  |  | X
Fan Status |  |  | X
Fan Command |  |  |  | X
Damper Output |  |  |  | X
Heating Command |  |  |  |  | X
Cooling Command | [5 empty] | X
System Mode | [5 empty] | X
Supply Air Temperature | [6 empty] | X
Zone Temperature Setpoint | [6 empty] | X
Zone Setpoint Bias | [6 empty] | X
Occupied Cooling Setpoint | [6 empty] | X
Unoccupied Cooling Setpoint | [6 empty] | X
Occupied Heating Setpoint | [6 empty] | X
Unoccupied Heating Setpoint | [6 empty] | X
Cooling Outside Air Lockout | [6 empty] | X
Supply Airflow Setpoint | [6 empty] | X
Cooling Maximum Flow | [6 empty] | X
Cooling Minimum Flow | [6 empty] | X
Cooling Unoccupied Flow | [6 empty] | X
Heat Maximum Flow | [6 empty] | X
Heating Minimum Flow | [6 empty] | X
Heating Unoccupied Flow | [6 empty] | X
Cool Down Minimum Flow | [6 empty] | X
Warm Up Minimum Flow | [6 empty] | X
System Mode | [6 empty] | X
Occupancy Command | [6 empty] | X
[8 empty] | VAV Duel Duct | 33 | 8 | 2 | 3 | 0 | 2 | 18
VAV Duel Duct
Description | NAME | AI | BI | AO | BO | NVR | NVW
Cooling Flow Ring Diff Pressure |  | X
Heating Flow Ring Diff Pressure |  | X
Cold Duct Temperature |  | X
Hot deck Temperature |  | X
Zone Temperature |  | X
Discharge Air Temperature |  | X
Warmer/Cooler Adjust |  | X
CO2 Sensor |  | X
Temporary Occupancy Button |  |  | X
Fan Status |  |  | X
Fan Command |  |  |  | X
Heating Damper Output |  |  |  | X
Cooling Damper Output |  |  |  | X
Cooling Command | [5 empty] | X
System Mode | [5 empty] | X
Supply Air Temperature | [6 empty] | X
Zone Temperature Setpoint | [6 empty] | X
Zone Setpoint Bias | [6 empty] | X
Occupied Cooling Setpoint | [6 empty] | X
Unoccupied Cooling Setpoint | [6 empty] | X
Occupied Heating Setpoint | [6 empty] | X
Unoccupied Heating Setpoint | [6 empty] | X
Cooling Outside Air Lockout | [6 empty] | X
Supply Airflow Setpoint | [6 empty] | X
Cooling Maximum Flow | [6 empty] | X
Cooling Minimum Flow | [6 empty] | X
Cooling Unoccupied Flow | [6 empty] | X
Heat Maximum Flow | [6 empty] | X
Heating Minimum Flow | [6 empty] | X
Heating Unoccupied Flow | [6 empty] | X
Cool Down Minimum Flow | [6 empty] | X
Warm Up Minimum Flow | [6 empty] | X
Occupancy Command | [6 empty] | X
[8 empty] | VAV Parallel | 30 | 5 | 2 | 3 | 0 | 2 | 18
VAV Parallel
Description | NAME | AI | BI | AO | BO | NVR | NVW
Flow Ring Diff Pressure |  | X
Zone Temperature |  | X
Discharge Air Temperature |  | X
Warmer/Cooler Adjust |  | X
CO2 Sensor |  | X
Temporary Occupancy Button |  |  | X
Fan Status |  |  | X
Fan Command |  |  |  | X
Damper Output |  |  |  | X
Heating Valve |  |  |  | X
Cooling Command | [5 empty] | X
System Mode | [5 empty] | X
Supply Air Temperature | [6 empty] | X
Zone Temperature Setpoint | [6 empty] | X
Zone Setpoint Bias | [6 empty] | X
Occupied Cooling Setpoint | [6 empty] | X
Unoccupied Cooling Setpoint | [6 empty] | X
Occupied Heating Setpoint | [6 empty] | X
Unoccupied Heating Setpoint | [6 empty] | X
Cooling Outside Air Lockout | [6 empty] | X
Supply Airflow Setpoint | [6 empty] | X
Cooling Maximum Flow | [6 empty] | X
Cooling Minimum Flow | [6 empty] | X
Cooling Unoccupied Flow | [6 empty] | X
Heat Maximum Flow | [6 empty] | X
Heating Minimum Flow | [6 empty] | X
Heating Unoccupied Flow | [6 empty] | X
Cool Down Minimum Flow | [6 empty] | X
Warm Up Minimum Flow | [6 empty] | X
Occupancy Command | [6 empty] | X
[8 empty] | Pump Constant | 3 | 0 | 1 | 0 | 1 | 1 | 0
Pump Constant
Description | NAME | AI | BI | AO | BO | NVR | NVW
Chiller Pump 1 Status |  |  | X
Chiller Pump 1 Command |  |  |  |  | X
Chiller Pump 1 Alarm | [5 empty] | X
[8 empty] | Pump Variable | 6 | 1 | 2 | 2 | 1 | 0 | 0
Pump Variable
Description | NAME | AI | BI | AO | BO | NVR | NVW
Differential Pressure Sensor |  | X
Pump Status |  |  | X
Pump Alarm |  |  | X
Pump Speed |  |  |  | X
Bypass Valve |  |  |  | X
Pump Command |  |  |  |  | X
[8 empty] | VFD | 7 | 1 | 1 | 0 | 0 | 5 | 0
VFD
Description | NAME | AI | BI | AO | BO | NVR | NVW
Speed |  | X
Remote Start/Stop |  |  | X
VFD Alarm | [5 empty] | X
VFD Status | [5 empty] | X
KW | [5 empty] | X
Power | [5 empty] | X
Run Hours | [5 empty] | X
[8 empty] | Ex-Fan Constant | 3 | 0 | 1 | 0 | 1 | 0 | 1
Ex-Fan Constant
Description | NAME | AI | BI | AO | BO | NVR | NVW
Exhaust Fan Status | EF-S |  | X
Exhaust Fan Command | EF-C |  |  |  | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Ex-Fan Temp Control | 8 | 1 | 1 | 0 | 1 | 0 | 5
Ex-Fan Temp Control
Description | NAME | AI | BI | AO | BO | NVR | NVW
Zone Temperature | ZN-T | X
Exhaust Fan Status | EF-S |  | X
Exhaust Fan Command | EF-C |  |  |  | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Ex-Fan Temp Control VFD | 9 | 1 | 1 | 1 | 1 | 0 | 5
Ex-Fan Temp Control VFD
Description | NAME | AI | BI | AO | BO | NVR | NVW
Zone Temperature | ZN-T | X
Exhaust Fan Status | EF-S |  | X
Exhaust Fan Speed | EF-O |  |  | X
Exhaust Fan Command | EF-C |  |  |  | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Ex-Fan PSI Control VFD | 6 | 1 | 1 | 1 | 1 | 0 | 2
Ex-Fan PSI Control VFD
Description | NAME | AI | BI | AO | BO | NVR | NVW
Building Static Pressure | BLDG-STATIC-P | X
Exhaust Fan Status | EF-S |  | X
Exhaust Fan Speed | EF-O |  |  | X
Exhaust Fan Command | EF-C |  |  |  | X
Static Pressure Setpoint | [6 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Condensing | 17 | 3 | 3 | 1 | 2 | 1 | 7
Condensing
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Heating Supply Water Temperature | HTG-SPLY-WTR-T | X
Heating Return Water Temperature | HTG-RTN-WTR-T | X
Emergency Stop Button | EMGCY-STP |  | X
Boiler Alarm | BOILER-ALM |  | X
Heating Pump 1 Status | HTG-PMP1-S |  | X
Heating Water Temperature Output | HTG-WTR-O |  |  | X
Boiler Command | BOILER-C |  |  |  | X
Heating Pump 1 Command | HTG-PMP1-C |  |  |  | X
Heating Outside Air Lockout | HTG-OSA-LOCK |  |  |  |  | X
Boiler Enable | BOILER-EN | [5 empty] | X
Heating Water High Setpoint | HTG-WTR-HI-SP | [5 empty] | X
Heating Water Low Setpoint | HTG-WTR-LO-SP | [5 empty] | X
Outside Air High Setpoint | OSA-HI-SP | [5 empty] | X
Outside Air Low Setpoint | OSA-LO-SP | [5 empty] | X
Effective Heating Water Setpoint | EFF-HTG-WTR-SP | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Non-condensing | 18 | 3 | 3 | 2 | 2 | 0 | 8
Non-condensing
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Heating Supply Water Temperature | HTG-SPLY-WTR-T | X
Heating Return Water Temperature | HTG-RTN-WTR-T | X
Emergency Stop Button | EMGCY-STP |  | X
Boiler Alarm | BOILER-ALM |  | X
Heating Pump 1 Status | HTG-PMP1-S |  | X
Heating Water Mixing Valve | HTG-WTR-VLV |  |  | X
Heating Water Temperature Output | HTG-WTR-O |  |  | X
Boiler Command | BOILER-C |  |  |  | X
Heating Pump 1 Command | HTG-PMP1-C |  |  |  | X
Boiler Enable | BOILER-EN | [5 empty] | X
Heating Water High Setpoint | HTG-WTR-HI-SP | [5 empty] | X
Heating Water Low Setpoint | HTG-WTR-LO-SP | [5 empty] | X
Outside Air High Setpoint | OSA-HI-SP | [5 empty] | X
Outside Air Low Setpoint | OSA-LO-SP | [5 empty] | X
Effective Heating Water Setpoint | EFF-HTG-WTR-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Air-cooled | 16 | 3 | 1 | 1 | 1 | 3 | 7
Air-cooled
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Chilled Supply Water Temperature | CH-SPLY-WTR-T | X
Chilled Return Water Temperature | CH-RTN-WTR-T | X
Chiller Alarm | CHILLER-ALM |  | X
Chilled Water Temperature Output | CH-WTR-O |  |  | X
Chiller Enable | CHILLER-EN |  |  |  | X
Chiller Run Hours | [5 empty] | X
Chiller KW | [5 empty] | X
Chiller Power | [5 empty] | X
Chilled Water High Setpoint | CH-WTR-HI-SP | [5 empty] | X
Chilled Water Low Setpoint | CH-WTR-LO-SP | [5 empty] | X
Outside Air High Setpoint | OSA-HI-SP | [5 empty] | X
Outside Air Low Setpoint | OSA-LO-SP | [5 empty] | X
Effective Chilled Water Setpoint | EFF-CLG-WTR-SP | [5 empty] | X
Chiller Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Water Cooled | 18 | 5 | 1 | 1 | 1 | 3 | 7
Water Cooled
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Chilled Supply Water Temperature | CH-SPLY-WTR-T | X
Chilled Return Water Temperature | CH-RTN-WTR-T | X
Condenser Supply Water Temperature | CND-SPLY-WTR-T | X
Condenser Return Water Temperature | CND-RTN-WTR-T | X
Chiller Alarm | CHILLER-ALM |  | X
Chilled Water Temperature Output | CH-WTR-O |  |  | X
Chiller Enable | CHILLER-EN |  |  |  | X
Chiller Run Hours | [5 empty] | X
Chiller KW | [5 empty] | X
Chiller Power | [5 empty] | X
Chilled Water High Setpoint | CH-WTR-HI-SP | [5 empty] | X
Chilled Water Low Setpoint | CH-WTR-LO-SP | [5 empty] | X
Outside Air High Setpoint | OSA-HI-SP | [5 empty] | X
Outside Air Low Setpoint | OSA-LO-SP | [5 empty] | X
Effective Chilled Water Setpoint | EFF-CLG-WTR-SP | [5 empty] | X
Chiller Outside Air Lockout | CH-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Open Tower | 17 | 4 | 1 | 1 | 1 | 3 | 7
Open Tower
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Outside Air Humidity | OA-RH | X
Tower Supply Water Temperature | TWR-SPLY-WTR-T | X
Tower Return Water Temperature | TWR-RTN-WTR-T | X
Chiller Alarm | TWR-ALM |  | X
Tower Fan Output | TWR-FAN-O |  |  | X
Cooling Tower Enable | TOWER-EN |  |  |  | X
Tower Run Hours | [5 empty] | X
Tower KW | [5 empty] | X
Tower Power | [5 empty] | X
Tower Supply Water High Setpoint | TWR-WTR-HI-SP | [5 empty] | X
Tower Return Water Low Setpoint | TWR-WTR-LO-SP | [5 empty] | X
Outside Air High Setpoint | OSA-HI-SP | [5 empty] | X
Outside Air Low Setpoint | OSA-LO-SP | [5 empty] | X
Effective Tower Water Setpoint | EFF-TWR-WTR-SP | [5 empty] | X
Tower Outside Air Lockout | TWR-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Closed Tower | 20 | 5 | 1 | 1 | 3 | 3 | 7
Closed Tower
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Outside Air Humidity | OA-RH | X
Tower Sump Temperature | TWR-SUMP-T | X
Tower Supply Water Temperature | TWR-SPLY-WTR-T | X
Tower Return Water Temperature | TWR-RTN-WTR-T | X
Chiller Alarm | TWR-ALM |  | X
Tower Fan Output | TWR-FAN-O |  |  | X
Cooling Tower Enable | TOWER-EN |  |  |  | X
Tower Pump Command | TWR-PMP-CMD |  |  |  | X
Tower Heater Command | TWR-HTR-CMD |  |  |  | X
Tower Run Hours | [5 empty] | X
Tower KW | [5 empty] | X
Tower Power | [5 empty] | X
Tower Supply Water High Setpoint | TWR-WTR-HI-SP | [5 empty] | X
Tower Return Water Low Setpoint | TWR-WTR-LO-SP | [5 empty] | X
Outside Air High Setpoint | OSA-HI-SP | [5 empty] | X
Outside Air Low Setpoint | OSA-LO-SP | [5 empty] | X
Effective Tower Water Setpoint | EFF-TWR-WTR-SP | [5 empty] | X
Tower Outside Air Lockout | TWR-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | DHW | 5 | 1 | 1 | 0 | 2 | 0 | 1
DHW
Description | NAME | AI | BI | AO | BO | NVR | NVW
Hot Water Temperature | HW-T | X
Water Pump Status | WTR-HTR-PMP-S |  | X
Water Heater Pump Command | WTR-HTR-PMP-C |  |  |  | X
Water Heater Command | WTR-HTR-C |  |  |  | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Baseboard/HW | 6 | 1 | 0 | 1 | 1 | 0 | 3
Baseboard/HW
Description | NAME | AI | BI | AO | BO | NVR | NVW
Zone Temperature | ZN-T | X
Inferred Heater Output | IR-HEAT-O |  |  | X
Inferred Heater Command | IR-HEAT-C |  |  |  | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Baseboard/Elec | 6 | 1 | 0 | 1 | 1 | 0 | 3
Baseboard/Elec
Description | NAME | AI | BI | AO | BO | NVR | NVW
Zone Temperature | ZN-T | X
Inferred Heater Output | IR-HEAT-O |  |  | X
Inferred Heater Command | IR-HEAT-C |  |  |  | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | FCU with Heat | 17 | 5 | 2 | 3 | 0 | 1 | 6
FCU with Heat
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outdoor Temperature |  | X
Zone Temperature |  | X
Discharge Air Temperature |  | X
Warmer/Cooler Adjust |  | X
CO2 Sensor |  | X
Temporary Occupancy Button |  |  | X
Fan Status |  |  | X
Fan Command |  |  |  | X
Damper Output |  |  |  | X
Heating Valve |  |  |  | X
System Mode | [5 empty] | X
Zone Temperature Setpoint | [6 empty] | X
Zone Setpoint Bias | [6 empty] | X
Occupied Heating Setpoint | [6 empty] | X
Unoccupied Heating Setpoint | [6 empty] | X
Heating Outside Air Lockout | [6 empty] | X
Occupancy Command | [6 empty] | X
[8 empty] | FCU with Heat/Cool | 21 | 5 | 2 | 4 | 0 | 0 | 10
FCU with Heat/Cool
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outdoor Temperature |  | X
Zone Temperature |  | X
Discharge Air Temperature |  | X
Warmer/Cooler Adjust |  | X
CO2 Sensor |  | X
Temporary Occupancy Button |  |  | X
Fan Status |  |  | X
Fan Command |  |  |  | X
Damper Output |  |  |  | X
Heating Valve |  |  |  | X
Cooling Valve |  |  |  | X
System Mode | [6 empty] | X
Zone Temperature Setpoint | [6 empty] | X
Zone Setpoint Bias | [6 empty] | X
Occupied Cooling Setpoint | [6 empty] | X
Unoccupied Cooling Setpoint | [6 empty] | X
Occupied Heating Setpoint | [6 empty] | X
Unoccupied Heating Setpoint | [6 empty] | X
Cooling Outside Air Lockout | [6 empty] | X
Heating Outside Air Lockout | [6 empty] | X
Occupancy Command | [6 empty] | X
[8 empty] | UH | 5 | 1 | 0 | 0 | 1 | 0 | 3
UH
Description | NAME | AI | BI | AO | BO | NVR | NVW
Zone Temperature | ZN-T | X
Heater Command | HEAT-C |  |  |  | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | IR Heaters | 5 | 1 | 0 | 0 | 1 | 0 | 3
IR Heaters
Description | NAME | AI | BI | AO | BO | NVR | NVW
Zone Temperature | ZN-T | X
Inferred Heater Command | IR-HEAT-C |  |  |  | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | PTAC | 14 | 1 | 1 | 0 | 4 | 0 | 8
PTAC
Description | NAME | AI | BI | AO | BO | NVR | NVW
Zone Temperature | ZN-T | X
Temporary Occupancy Button | TEMP-OCC |  | X
Supply Fan Command | SF-C |  |  |  | X
Cooling Command | CLG-C |  |  |  | X
Heating Stage 1 Command | HTG1-C |  |  |  | X
Heating Stage 2 Command | HTG2-C |  |  |  | X
Outside Air Temperature | OA-T | [5 empty] | X
Occupied Cooling Setpoint | OCC-CLG-SP | [5 empty] | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Cooling Setpoint | UNOCC-CLG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Heating Outside Air Lockout | HTG-OSA-LOCK | [5 empty] | X
Cooling Outside Air Lockout | CLG-OSA-LOCK | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Paddle Fans | 5 | 1 | 0 | 0 | 1 | 0 | 3
Paddle Fans
Description | NAME | AI | BI | AO | BO | NVR | NVW
Zone Temperature | ZN-T | X
Paddle Fan Command | PAD-FAN-C |  |  |  | X
Occupied Heating Setpoint | OCC-HTG-SP | [5 empty] | X
Unoccupied Heating Setpoint | UNOCC-HTG-SP | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Building Energy | 4 | 0 | 0 | 0 | 0 | 4 | 0
Building Energy
Description | NAME | AI | BI | AO | BO | NVR | NVW
Total Metered Building kW | [5 empty] | X
Total Building Water Usage | [5 empty] | X
Total Building Natural Gas Usage | [5 empty] | X
Total Building Propane Usage | [5 empty] | X
[8 empty] | Gas Meter | 6 | 1 | 0 | 0 | 0 | 5 | 0
Gas Meter
Description | NAME | AI | BI | AO | BO | NVR | NVW
Pulse Count |  | X
Hourly usage | [5 empty] | X
Daily Usage | [5 empty] | X
Weekly Usage | [5 empty] | X
Monthly usage | [5 empty] | X
Yearly usage | [5 empty] | X
[8 empty] | Water Meter | 6 | 1 | 0 | 0 | 0 | 5 | 0
Water Meter
Description | NAME | AI | BI | AO | BO | NVR | NVW
pulse Count |  | X
Hourly usage | [5 empty] | X
Daily Usage | [5 empty] | X
Weekly Usage | [5 empty] | X
Monthly usage | [5 empty] | X
Yearly usage | [5 empty] | X
[8 empty] | Electric Meter | 12 | 0 | 0 | 0 | 0 | 12 | 0
Electric Meter
Description | NAME | AI | BI | AO | BO | NVR | NVW
A-Phase Voltage | [5 empty] | X
B-Paseo Voltage | [5 empty] | X
C-Phase Voltage | [5 empty] | X
A-Phase Amperage | [5 empty] | X
B-Paseo Amperage | [5 empty] | X
C-Phase Amperage | [5 empty] | X
Power | [5 empty] | X
Hourly usage | [5 empty] | X
Daily Usage | [5 empty] | X
Weekly Usage | [5 empty] | X
Monthly usage | [5 empty] | X
Yearly usage | [5 empty] | X
[8 empty] | PV | 7 | 1 | 1 | 0 | 2 | 3 | 0
PV
Description | NAME | AI | BI | AO | BO | NVR | NVW
Panel Temp |  | X
Remote Start/Stop |  |  | X
Inverter Alarm |  |  |  |  | X
Inverter Status |  |  |  |  | X
KW | [5 empty] | X
Power | [5 empty] | X
Run Hours | [5 empty] | X
[8 empty] | Thermal | 13 | 6 | 1 | 1 | 1 | 2 | 2
Thermal
Description | NAME | AI | BI | AO | BO | NVR | NVW
Outside Air Temperature | OA-T | X
Solar Supply Water Temperature | SOL-SPLY-WTR-T | X
Solar Return Water Temperature | SOL-RTN-WTR-T | X
Tank Temperature | TANK-T | X
Tank Supply Water Temperature | TNK-SPLY-WTR-T | X
Tank Return Water Temperature | TNK-RTN-WTR-T | X
Pump Alarm | PMP-ALM |  | X
Mixing Valve Output | MIX-VLV-O |  |  | X
Pump Enable | PMP-EN |  |  |  | X
Loop BTU | [5 empty] | X
Chiller Power | [5 empty] | X
Solar Water Setpoint | SOL-WTR-SP | [5 empty] | X
Occupancy Command | OCC-C | [5 empty] | X
[8 empty] | Lights | 2 | 0 | 0 | 0 | 2 | 0 | 0
Lights
Description | NAME | AI | BI | AO | BO | NVR | NVW
Command | LGHT-C |  |  |  | X
Status | LGHT-S |  |  |  | X

## System Health (hidden)
| Total Pass | Total Fail | Pct. Passed | System Avg. Passed
Temperature Sensors | 0 | 0 | 0% | #DIV/0!
Damper Positions | 0 | 0 | 0%
Fan/Pump Control | 0 | 0 | 0%
Enable / Disable | 0 | 0 | 0%
Heating Control | 0 | 0 | 0%
Cooling Control | 0 | 0 | 0%
Economizer Control | 0 | 0 | 0%
Humidity Sensor | 0 | 0 | 0%
Multi-Gas Sensors | 0 | 0 | 0%
Communication Status | 0 | 0 | 0%

## Points List (hidden)
Equipment | Qty | Pts/Ea | Total Pts | AI | BI | AO | BO | NVR | NVW | AI | BI | AO | BO | NVR | NVW | Sum of Pieces of Equipment
AHU HW/CW | 0 | 32 | 0 | 10 | 5 | 3 | 2 | 3 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AHU HW/DX | 0 | 37 | 0 | 10 | 5 | 3 | 2 | 4 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | Total Points
AHU HW Only | 0 | 34 | 0 | 11 | 7 | 4 | 2 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AHU Elec/CW | 0 | 34 | 0 | 11 | 7 | 4 | 2 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | Hardware Pts
AHU Elec/DX | 0 | 34 | 0 | 11 | 7 | 4 | 2 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AHU Elec Heat Only | 0 | 34 | 0 | 11 | 7 | 4 | 2 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0
MAU with Heat | 0 | 20 | 0 | 4 | 4 | 2 | 2 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | AI | 0
MAU with Heat/Cool | 0 | 20 | 0 | 4 | 4 | 2 | 2 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | BI | 0
Energy Recovery Unit | 0 | 18 | 0 | 6 | 4 | 4 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | AO | 0
Water Source HP | 0 | 13 | 0 | 2 | 1 | 0 | 6 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | BO | 0
Gas Furnace | 0 | 13 | 0 | 4 | 1 | 0 | 3 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | NVR | 0
Electric Furnace | 0 | 13 | 0 | 4 | 1 | 0 | 3 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | NVW | 0
Split System AC/Elec Heat | 0 | 18 | 0 | 5 | 1 | 0 | 4 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Split System AC/Gas Heat | 0 | 17 | 0 | 5 | 1 | 0 | 3 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
RTU Eccon 1 Cool/Elc | 0 | 20 | 0 | 7 | 1 | 1 | 3 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
RTU Eccon 2 Cool/Elc | 0 | 22 | 0 | 7 | 1 | 1 | 5 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
RTU Eccon 1 Cool/Gas | 0 | 20 | 0 | 7 | 1 | 1 | 3 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
RTU Eccon 1 Cool/Gas Mod | 0 | 21 | 0 | 7 | 1 | 2 | 3 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
RTU Eccon 2 Cool/Gas | 0 | 21 | 0 | 7 | 1 | 1 | 4 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
RTU Eccon 2 Cool/Gas Mod | 0 | 22 | 0 | 7 | 1 | 2 | 4 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
RTU 1 Cool/Elc | 0 | 18 | 0 | 6 | 1 | 0 | 3 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
RTU 2 Cool/Elc | 0 | 20 | 0 | 6 | 1 | 0 | 5 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
RTU 1 Cool/Gas | 0 | 18 | 0 | 6 | 1 | 0 | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RTU 1 Cool/Gas Mod | 0 | 19 | 0 | 6 | 1 | 1 | 3 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
RTU 2 Cool/Gas | 0 | 19 | 0 | 6 | 1 | 1 | 3 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
RTU 2 Cool/Gas Mod | 0 | 19 | 0 | 6 | 1 | 0 | 4 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
RTU 2 Cool/Gas Mod | 0 | 19 | 0 | 6 | 1 | 0 | 4 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Zone DA-T Control | 0 | 15 | 0 | 3 | 1 | 1 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0
Zone Room Control | 0 | 11 | 0 | 3 | 1 | 1 | 0 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 0
VAV No Fan/No Reheat | 0 | 27 | 0 | 5 | 1 | 1 | 0 | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0
VAV Reheat/Water | 0 | 28 | 0 | 5 | 1 | 2 | 0 | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0
VAV Reheat/Elec | 0 | 28 | 0 | 5 | 1 | 1 | 1 | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0
VAV Fan Pow/Water | 0 | 30 | 0 | 5 | 2 | 3 | 0 | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0
VAV Fan Pow/Elec. | 0 | 30 | 0 | 5 | 2 | 2 | 1 | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0
VAV Duel Duct | 0 | 33 | 0 | 8 | 2 | 3 | 0 | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0
VAV Parallel | 0 | 30 | 0 | 5 | 2 | 3 | 0 | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0
Pump Constant | 0 | 3 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pump Variable | 0 | 6 | 0 | 1 | 2 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VFD | 0 | 7 | 0 | 1 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ex-Fan Constant | 0 | 3 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Ex-Fan Temp Control | 0 | 8 | 0 | 1 | 1 | 0 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0
Ex-Fan Temp Control VFD | 0 | 9 | 0 | 1 | 1 | 1 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0
Ex-Fan PSI Control | 0 | 8 | 0 | 1 | 1 | 0 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0
Ex-Fan PSI Control VFD | 0 | 6 | 0 | 1 | 1 | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0
Condensing | 0 | 17 | 0 | 3 | 3 | 1 | 2 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 0
Non-condensing | 0 | 18 | 0 | 3 | 3 | 2 | 2 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Electric | 0 | 16 | 0 | 3 | 1 | 1 | 1 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0
Air-cooled | 0 | 16 | 0 | 3 | 1 | 1 | 1 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0
Water Cooled | 0 | 18 | 0 | 5 | 1 | 1 | 1 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0
Open Tower | 0 | 17 | 0 | 4 | 1 | 1 | 1 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0
Closed Tower | 0 | 20 | 0 | 5 | 1 | 1 | 3 | 3 | 7 | 0 | 0 | 0 | 0 | 0 | 0
DHW | 0 | 5 | 0 | 1 | 1 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Baseboard/HW | 0 | 6 | 0 | 1 | 0 | 1 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0
Baseboard/Elec | 0 | 6 | 0 | 1 | 0 | 1 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0
FCU with Heat | 0 | 17 | 0 | 5 | 2 | 3 | 0 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0
FCU with Heat/Cool | 0 | 21 | 0 | 5 | 2 | 4 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0
UH | 0 | 5 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0
IR Heaters | 0 | 5 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0
PTAC | 0 | 14 | 0 | 1 | 1 | 0 | 4 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0
Paddle Fans | 0 | 5 | 0 | 1 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0
Building Energy | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Meter | 0 | 6 | 0 | 1 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas Meter | 0 | 6 | 0 | 1 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electric Meter | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV | 0 | 7 | 0 | 1 | 1 | 0 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Thermal | 0 | 13 | 0 | 6 | 1 | 1 | 1 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0

## OM_List
O&M Deficiencies
Notes:
FACID | Building | Equipment | Fault | Fixes | Fix Cost Estimate
Total |  |  |  |  | 0

## OM_Examples
Common O&M Deficiencies
This list is shows examples of common O&M deficiencies. This list is not comprehensive. It is primarily meant as a guide to help users document the appropriate amount of detail for O&M deficiencies.
Component | Fault
Chiller System | System leaks in piping
Chiller System | Fouling
Chiller System | Low/High refrigerant charge
Chiller System | Short-cycling
Chiller System | Manual Isolation valves partially closed
Chiller System | Automatic isolation valves missing or failed
Boiler System | Stack corrosion
Boiler System | Over/under firing
Boiler System | Fouling
Boiler System | System leaks in piping
Boiler System | Short-cycling
Boiler System | Manual Isolation valves partially closed
Boiler System | Automatic isolation valves missing or failed
Condenser Boiler | Return water > 130°F (no longer condensing)
Steam Boiler | Leaking Steam Traps, Condensate not returning
Pumps | Worn bearings or impellers
Pumps | Manually On/Off
Pumps | Suction fail / Cavitating
Pumps | Differential pressure station fail
VFD | Manually configured to HAND at VFD keypad
VFD | Turned off
VFD | Offline
VFD | Maximum Speed Parameters reduced
VFD | Minimum Speed Parameter matches Maximum Speed
Cool/Heat Coils | Fouling (air-side or water-side)
Cool/Heat Coils | Failed actuator (loss of 24VAC power, loose/disconnected control wires)
Cool/Heat Coils | Valve manually positioned (either from the electric valve actuator or from the field controller - both typically come with manual bypass capabilities)
Cool/Heat Coils | Valve leak
Cool/Heat Coils | Manual Isolation valves partially closed
Cool/Heat Coils | Balancing valves improperly configured
Dampers | Broken vanes/damper blades/linkages
Dampers | Failed actuator (loss of 24VAC power, loose/disconnected control wires)
Dampers | Manually positioned (either from the electric valve actuator or from the field controller - both typically come with manual bypass capabilities)
Dampers | Damper leak
Dampers | Automatic Fire/Smoke dampers closed
Dampers | Balancing dampers improperly configured
Air Supply | Duct leaks
Air Supply | Duct blockages
Air Supply | Dirty filters, coils or intake bird screens
Air Supply | Duct static station fail
Fan | Worn bearings
Fan | Worn belt
Fan | Manually On/Off
BCS | Offline controller
BCS | Failed sensors
BCS | Lack of network access (controllability)
BCS | Equipment doesn't respond to commands

## Integration Ready Definition
1. Fully Integration Ready Requirements:
1.1 | Enduring: Not on a list for demolition or for a major renovation, nor listed for real property disposal within five years after the SRA.
1.2 | The EBCS JACE must be a JACE 8050 with a Niagara 4.3.58 license or higher. It is permitted for the local BCS front-end (NAC) to also be the EBCS JACE if it meets the hardware and software license requirements. It is also permitted for an MDMS JACE to be the EBCS JACE if it meets the hardware and software license requirements.
2. Potential Integration Ready Candidates’ Requirements:
2.1 | Enduring: Not on a list for demolition or for a major renovation nor listed for real property disposal within five years after the SRA.
2.2 | The BCS shall communicate in an open protocol that is common with current BCS standards. The two that are the most common for BCS’s are BACNET and LON. Most control systems installed after 2005 utilize one of these communication protocols.
3. Not Integration Ready:
3.1 | Systems that do not meet either fully integration ready requirements or are potential integration ready candidates are deemed as not integration ready. Systems that are not integration ready may require significant upgrades to the HVAC and/or BCS.
4. Functional and Completeness Considerations:
4.1 | The criteria listed as “Functional and Completeness Considerations” must be met for the system to achieve a high-level of functionality and BCS completeness. The minimum standards that must be met for the functional considerations are under the discretion of each Readiness Division.
4.2 | The existing BCS was installed later than 2005.
a. BCSs that were installed before 2005 maybe accepted on a building-by-building basis.
b. Both hardware and software product that are installed in the building are still supported by the manufacture or a local Contractor.
4.3 | A building level control system (BCS) installed in the building that controls all major HVAC equipment. Major HVAC equipment that is typically connected to the BCS are, but not limited to:
a. Air handler units
b. Packaged or rooftop heating and cooling systems
c. Source of cooling for the building (e.g. chillers)
d. Source of heating for the building (e.g. boilers)
e. Zone/ Space/ Room temperature controls
f. Exhaust fans
4.4 | Optional equipment may be integrated into the BCS but are not necessary for enterprise integration. Optional equipment that may also be integrated into the BCS are:
a. Lighting systems
b. Electric, Gas, and Water meters
c. Renewables
d. Emergency generation
4.5 | The BCS shall communicate in an open protocol that is common with current BCS standards. The two that are the most common for BCS’s are BACNET and LON. Most control systems installed after 2005 utilize one of these communication protocols.
4.6 | The BCS shall have the ability to be configured to allow the enterprise integration controller to read and write to data points within the system.
4.7 | BCS points list with read and write points (analog inputs and analog outputs, digital/binary inputs and outputs, virtual inputs and outputs). Shall have the current point naming conventions.
a. Manufacture of the hardware in the BCS
b. Manufacture of the software in the BCS
c. Current version of software that is installed in the BCS
d. Last software update

## Integration Ready Status
Integration Ready Status
Integration Ready Requirements | Responses: | Notes:
Is the facility enduring and not considered for demolition, major renovation, or real property disposal within five years after the SRA?
Does the BCS front-end use a Jace or other vendor?
If Jace, what is the model?
If Jace, what is the Niagara version?
Does the BCS have an open license that allows all controllable points to be writable?
Does the BCS point list follow the EBCS naming convention?
Do the BCS graphics follow the EBCS graphics standards?
Additional Comments:
Estimated Integration Ready Results

## Entry Lists (hidden)
Pass | Enduring
Fail | Not Enduring
N/A | Jace
Other Vendor
AHU HW/CW | BACnet
AHU HW/DX | LON
AHU HW Only | Yes
AHU Elec/CW | No
AHU Elec/DX | Partially
AHU Elec Heat Only | Unknown
MAU with Heat | On BCS
MAU with Heat/Cool | In Building, but not on BCS
Energy Recovery Unit | Does not exist
600
Water Source HP | 600E
Gas Furnace | 7000
Electric Furnace | 8000
8050
Split System AC/Elec Heat | 8200
Split System AC/Gas Heat | Below 3.8
3.8
RTU Eccon 1 Cool/Elc | N4
RTU Eccon 2 Cool/Elc | N4.3+
RTU Eccon 1 Cool/Gas
RTU Eccon 1 Cool/Gas Mod
RTU Eccon 2 Cool/Gas
RTU Eccon 2 Cool/Gas Mod
RTU 1 Cool/Elc
RTU 2 Cool/Elc
RTU 1 Cool/Gas
RTU 1 Cool/Gas Mod
RTU 2 Cool/Gas
RTU 2 Cool/Gas Mod
RTU 2 Cool/Gas Mod
Zone DA-T Control
Zone Room Control
VAV No Fan/No Reheat
VAV Reheat/Water
VAV Reheat/Elec
VAV Fan Pow/Water
VAV Fan Pow/Elec.
VAV Duel Duct
VAV Parallel
Pump Constant
Pump Variable
VFD
Ex-Fan Constant
Ex-Fan Temp Control
Ex-Fan Temp Control VFD
Ex-Fan PSI Control
Ex-Fan PSI Control VFD
Condensing
Non-condensing
Electric
Air-cooled
Water Cooled
Open Tower
Closed Tower
DHW
Baseboard/HW
Baseboard/Elec
FCU with Heat
FCU with Heat/Cool
UH
IR Heaters
PTAC
Paddle Fans
Building Energy
Water Meter
Gas Meter
Electric Meter
PV
Thermal
Lights

## Costs Notes (hidden)
1 | Integration Costs
2 | Cost to Bring BCS to Integration Ready
3 | Cost to Improve Control Capabilities
1 | If integration ready and needs to be integrated to EBCS
Material Costs
Network drop/cables/switch
Labor Costs
Establishing connection to EBCS
Integrating points and graphics to EBCS
Integrating station to existing EBCS framework (State & RD pages, sustainment logs?, etc)
2 | Cost to Bringing BCS to Integration Ready Status
Material Costs
Jace 8000 with N4.3.## license, enclosure, transformer
Network drop/cables/switch
Local workstation with workbench license
Labor Costs
Jace installation and commissioning
Opening points or acquiring open license from NAC vendor
Integrating BCS to IC Jace w naming convention and graphics
Potentially needs station migration if upgrading Jaces/Softwares
Adding IC Jace to ARNET
Installing local workstation with workbench license and connecting to Jace
3 | Cost to Improve Control Capabilities
Material Costs
Equipment upgrades
Equipment controller upgrades
Replacing local BCS front-end with Jace 8000 (N4.3.##)
Parts for physical equipment repairs (O&M)
Sensor replacement or calibration
Labor Costs
Integrating equipment or controller upgrades to BCS
Integrating existing equipment not on BCS to BCS
Replacing front-end
Jace installation and commissioning
Configuring new station with naming convention, sequencing, graphics
Adding to ARNET
Physical equipment repairs (O&M)
Releasing physical equipment overrides
Sensor replacement or calibration

## Level of Completeness
Level of Completeness
Please provide a "Low, Med, or High" response in the box above to assess the current level of completeness based on the information entered below. For example: if the BCS has all of the major HVAC equipment integrated, then a "High" status would be entered.
Considerations: | Responses: | Notes
What is the vintage (year) of the BCS?
Does the BCS communicate with BACnet or LON?
What percentage of the facility SQFT is controlled by the BCS?
Are all major HVAC components on the BCS?
Air handling units?
Packaged or rooftop systems?
Cooling source (ex: chillers)
Heating source (ex: boilers)
Zone temperature controls?
Exhaust fans?
Is lighting on the BCS?
Are any utility meters on the BCS?
Electric meter?
Gas meter?
Water meter?
Is the MDMS controller a Jace or other vendor?
If Jace, what is the model?
If Jace, what is the Niagara version?
Is the Jace already integrated into the BCS?
Are any renewables or co-generation systems on the BCS?
Are these systems submetered?
What is the vendor, model, software version of the controller?
Is the RE controller already integrated into the BCS?
Additional Potential Building Systems:
Occupancy sensors?
Domestic hot water heating?
Water treatment?
Fire alarms and suppression?
Other?
Additional Comments:
Highlights of observed performance of BCS-connected equipment
List any issues, obstacles or possible show stoppers.
Other

## int_ready_calcs (hidden)
Criteria | Calcs | Good | Max Pts | Integration Ready Status | Full | Partial
Is the facility enduring and not considered for demolition, major renovation, or real property disposal? | 0 | Enduring | 1 | items | 7 | 5
Does the BCS front-end use a Jace or other vendor? | 0 |  | 1 | ready | #REF!
If Jace, what is the model? | #REF! | 8200 | 1 | no | #REF!
If Jace, what is the Niagara version? | 0 | 4 | 1 | partial, pts/graphics | #REF!
Does the BCS have an open license that allows all controllable points to be writable? | 0 |  | 1 | partial, other | #REF!
Does the BCS point list follow the EBCS naming convention? | 0 |  | 1
Do the BCS graphics follow the EBCS graphics standards? | 0 |  | 1
NO
This system is not integration ready. Review the Integration Ready Definition for priority action items.
YES
Ready for Integration
MAYBE
Partially integration ready. Needs additional work to become integration ready.
Partially integration ready. Graphics and point names do not follow naming convention
STATUS
#REF!

## Onsite Checklist
Onsite Checklist |  | #REF!
General Building Information | Responses:
Site FAC ID:
Building Number/Name(field use):
Building Name/Type:
Facility Number(RPI):
Building sq. ft.
Photos of buildings, BCS and meters as outlined below
Building Contact Name and Phone Number
NAC Assessment | Responses:
How many NACs are in the building? (Take Pictures)
Are any NACs connected to the ARNET?
What is/are the IP address(es)?
Does the NAC currently have an open license?
Which tools were used to verify all points were open and commendable?
Did any of the points need to be opened while onsite? If so, which points?
Do any of the points still need to be opened? If so, which points?
Why weren't these points opened during the site visit?
What communications protocol does the system use?
What is the hardware brand and version of the NAC?
What is the software name and version of the NAC?
Are there any existing mechanical issues?
Are the field controllers communicating with the BCS?
What brand are the field controllers? (Take Pictures)
Is the NAC integration ready? (No additional work is required by a BCS contractor.)
If not integration ready, how many Jaces will be needed for integration?
Additional NAC Comments:
WAN Connection Assessment | Responses:
How far is the IT closet from the NAC/EBCS Jace? (Take Pictures)
Is the network connection greater than 300 feet from the NAC/EBCS Jace?
Is there underground communication conduit available?
Is there communication infrastructure in place between buildings that can be used to connect building BCSs?
Additional WAN network Comments:
Floorplan:
Obtained floorplans
Verify floorplans reflect actual layout
Mark the floorplans listing the IT rooms, NAC locations, and the mechanical room locations
Additional Floorplan Comments:
HVAC Equipment
Mechanical drawings obtained
Which major HVAC components are in the facility?
Air handling units? Qty?
Packaged or rooftop systems? Qty?
Cooling source (ex:chillers)? Qty?
Heating source (ex:boilers)? Qty?
Zone temperature controls? Qty?
Exhaust fans? Qty?
Other? Qty?
Confirm the BCS equipment list is up to date (Compare equipment on Mechanical drawings and BCS equipment list)
Are any renewable energy technologies present? If so, which?
Are any of these systems on the BCS? If so, which?
If any systems (HVAC or RE) are not on BCS, use Preliminary Costs Part C to identify tasks and cost to integrate to BCS.
Highlights of observed performance of HVAC equipment (Take Pictures)
List any issues, obstacles or possible show stoppers (Take Pictures)
Additional Comments

## Utility Meters and MDMS
Utility Meters and MDMS |  | #REF!
Electrical Meter Assessment | Responses:
Is the utility owned electrical meter serving more than one building? If so list the buildings.
List the utility owned meter tag numbers for each electrical meter and building ID. (Take pictures.)
List which electrical meter/meters are monitored by MDMS?
Is any information available to specify which electrical circuit MDMS is monitoring?
Gas Meter Assessment | Responses:
What type of heating fuel source is serving the building? (For example natural gas or propane.)
Does the utility owned gas meter/meters serve more than one building? If so list buildings.
List the meter tag numbers for each gas meter and building ID. (Take Pictures)
Are the units per pulse labeled on the utility owned gas pulse meter? If so what are the units per pulse?
Is the gas monitored by MDMS?
Are the units per pulse labeled on the water pulse for MDMS?
Water Meter Assessment | Responses:
What is the primary water source for the building? (For example utilities or well)
Does the utility owned water meter/meters serve more than one building? If so list buildings.
List tag numbers for each utility owned water meter and building ID. (Take Pictures)
Are the units per pulse labeled on the utility owned water pulse meter? If so what are the units per pulse?
Is the water monitored by MDMS?
Are the units per pulse labeled on the water pulse for MDMS?
Additional Utility Meter Comments:
MDMS Jace and/or Utility Meter Integration Assessment | Responses:
Is an MDMS Jace present?
If there is an MDMS Jace:
What is the model and niagara software version of the MDMS Jace?
What is the IP address and username/password?
Are all utility meters connected to the MDMS Jace? Which are and which are missing?
Are the connected meters correctly communicating and reporting to the MDMS Jace?
Where is the MDMS Jace located?
Can the MDMS Jace be used as an EBCS Jace?
If the MDMS Jace cannot be used as an EBCS Jace, how far are they from each other?
If there is NOT an MDMS Jace:
Are there physical factors limiting the utility meters from being integrated into the EBCS Jace?
How far are the meters from the EBCS Jace?
Are there any technical factors limiting the utility meters from being integrated into the EBCS Jace?
Reminder: Include costs for integrating utility meters to local BCS/NAC or EBCS Jace in the Preliminary Costs tab.
Additional MDMS Comments:

## Preliminary Costs
Preliminary Costs
The tasks on this sheet are suggestive and primarily provide a framework template for cost-breakdown needs. The items on this sheet are not comprehensive, and not all items will be applicable to all systems. Review the Instructions tab for further guidance.
Building Integration Status Assessment | 0
Part A. Costs for enabling integration: This section itemizes costs that enable integration through upgrading the system to "Integration Ready" status or through installing a qualified EBCS JACE.
Task | Material Costs |  |  |  | Labor Costs |  | Sum $
| Item | $/ea. | Qty. | Item $ Total | Labor Type | Labor $ Total
Option 1: Using existing BCS (NAC) as EBCS JACE (applicable for buildings with local BCS front-end (NAC) qualified for EBCS JACE)
Opening points or acquiring open license for NAC | [6 empty] | 0
Other | [6 empty] | 0
Other | [6 empty] | 0
Other | [6 empty] | 0
Option 2: Add an EBCS Jace (applicable for systems that has local BCS (NAC) qualified for EBCS Jace and/or systems that are compatible with a qualified EBCS Jace)
Installing Jace 8200 with N4.8.## license, NEMA enclosure, and 24 VAC transformer, commissioning Jace | [6 empty] | 0
0
0
0
0
0
0
0
Opening points or acquiring open license for NAC | [6 empty] | 0
Integrating NAC to EBCS Jace | [6 empty] | 0
Other | [6 empty] | 0
Other | [6 empty] | 0
Other | [6 empty] | 0
Option 3: Replacing local BCS front-end with Jace 8200 (applicable for systems that do not have local BCS (NAC) as EBCS Jace and/or systems that are compatible with an EBCS Jace)
Option 3: Replacing local BCS front-end with Jace 8200 (N4.8.##) to use as both NAC and EBCS Controller, NEMA enclosure, and 24 VAC transformer, commissioning Jace | [6 empty] | 0
0
0
0
0
0
0
0
Configure new station or migrate existing station | [6 empty] | 0
Opening points or acquiring open license for NAC | [6 empty] | 0
Other | [6 empty] | 0
Other | [6 empty] | 0
Option 4: Use MDMS Jace as EBCS Jace (applicable for systems that have local BCS (NAC) qualified for EBCS Jace and/or systems that are compatible with a qualified EBCS Jace)
Opening points or acquiring open license for NAC
Integrating NAC to EBCS Jace
Configure new station or migrate existing station
Other
Other | [6 empty] | 0
Other | [6 empty] | 0
After selecting Part A, Option 1, 2, 3 or 4:
Installing any necessary network drops/cables/switches | [6 empty] | 0
0
0
0
0
Implement EBCS naming convention | [6 empty] | 0
Implement EBCS graphics on EBCS JACE | [6 empty] | 0
Connecting Jace to ARNET | [6 empty] | 0
Other | [6 empty] | 0
Other | [6 empty] | 0
Other | [6 empty] | 0
Total: Estimate preliminary costs for enabling Integration [Option 1] | 0 | [5 empty] | 0
Total: Estimate preliminary costs for enabling Integration [Option 2] | 0
Total: Estimate preliminary costs for achieving "Integration Ready" status [Option 3] | 0 |  |  |  | 0 |  | 0
Total: Estimate preliminary costs for achieving "Integration Ready" status [Option 4] | 0
Notes and Comments:
Part B. Utility Meter Integration Costs: This section itemizes costs to integrate the utility meters to the EBCS JACE
Task | Material Costs |  |  |  | Labor Costs |  | Sum $
| Item | $/ea. | Qty. | Item $ Total | Labor Type | Labor $ Total
Option 1: Removing the MDMS JACE and integrating the utility meters directly to the local BCS/NAC or EBCS Jace
Extending communication lines from the utility meters to the local BCS/NAC or EBCS JACE. | [6 empty] | 0
Establishing connection from EBCS Jace to EBCS | [6 empty] | 0
Integrating points and graphics to EBCS | [6 empty] | 0
Other | [6 empty] | 0
Option 2: Integrating the MDMS JACE to the local BCS/NAC or EBCS JACE
Extending communication lines from the MDMS JACE to the local BCS/NAC or EBCS JACE. | [6 empty] | 0
Establishing connection from EBCS Jace to EBCS | [6 empty] | 0
Integrating points and graphics to EBCS | [6 empty] | 0
Other | [6 empty] | 0
Total: Estimate preliminary costs for integrating utility meters to local BCS/NAC or EBCS JACE. [Option 1] | 0 |  |  |  | 0 |  | 0
Total: Estimate preliminary costs for integrating MDMS JACE to the local BCS/NAC or EBCS JACE. [Option 2] | 0 |  |  |  | 0 |  | 0
Notes and Comments:
Part C. EBCS Integration Costs: This section itemizes costs to integrate EBCS JACE to EBCS.
Task | Material Costs |  |  |  | Labor Costs |  | Sum $
| Item | $/ea. | Qty. | Item $ Total | Labor Type | Labor $ Total
Establishing connection from EBCS Jace to EBCS | [6 empty] | 0
Integrating station to EBCS | [6 empty] | 0
Converting points and graphics to EBCS standards | [6 empty] | 0
Integrating points and graphics to EBCS | [6 empty] | 0
Other | [6 empty] | 0
Other | [6 empty] | 0
Other | [6 empty] | 0
Other | [6 empty] | 0
Other | [6 empty] | 0
Other | [6 empty] | 0
Total Integration Costs | 0 |  |  |  | 0 |  | 0
Notes and Comments:
Part D. Costs for Improving Functionality and Completeness: These costs will increase the level of functionality within the system.
Task | Material Costs |  |  |  | Labor Costs |  | Sum $
| Item | $/ea. | Qty. | Item $ Total | Labor Type | Labor $ Total
Integrate Devices Not on BCS | [6 empty] | 0
Total Costs to Integrate Devices Not on BCS | [6 empty] | 0
Costs to improve existing BCS (e.g remove Trane Front End or replace defective JACE)
Total Costs to Improve Existing BCS
Summary of Costs from OM List | [6 empty] | 0
Total: Estimate preliminary costs for improving functionality and Completeness | [6 empty] | 0
Notes and Comments:

## Output
Site Information |  |  | System Health
Site FACID | 0 |  | Sensor / Control Point | Pass Percentage
Building Number | 0 |  | Temperature Sensors | 0%
Building Name | 0 |  | Damper Positions | 0%
SQFT | 0 |  | Fan/Pump Control | 0%
Site Contact | 0 |  | Enable - Disable | 0%
|  |  | Heating Control | 0%
|  |  | Cooling Control | 0%
|  |  | Economizer Control | 0%
|  |  | Humidity Sensor | 0%
|  |  | CO2 Sensor | 0%
|  |  | Communication Status | 0%
|  |  | Total System Health | #DIV/0!
Integration Ready Status |  |  |  |  | BCS / NAC Information
Integration Ready Status | 0 | Additional Comments from SRA |  |  | Network Controller | Network Software | Field Controller | IP Address | Communication protocol
Level of Functionality
Level of Functionality | #DIV/0! | Additional Comments from SRA |  |  | Equipment Count | Total Points | Total Hardware Points | AI | BI | AO | BO | NVR | NVW
Level of Completeness
Level of Functionality | 0% | Additional Comments from SRA |  |  | {NEED TO ENTER DATA; NOT AUTO CALCULATED}
Preliminary Integration Costs
PART A: Enable EBCS Integration Costs
Option 1: Using NAC as an EBCS JACE
Option 2: Install an EBCS JACE |  |  |  | 0
Option 3: Replacing local BCS front-end with Jace 8200
Option 4: Use MDMS Jace as EBCS Jace |  |  |  | 0
PART B: Utility Meter Integration
Option 1: Integrating utility meters to local BCS/NAC or EBCS Jace. |  |  |  | 0
Option 2: Integrating MDMS Jace to local BCS/NAC or EBCS Jace. |  |  |  | 0
PART C: EBCS Integration Costs
EBCS Integration Costs |  |  |  | 0
PART D: Costs for Improving Functionality / Completeness
Costs for improving/repairing HVAC functionality |  |  |  | 0
Explain which EBCS integration strategies listed above are recommended for the facility and provide justification. Under the plans and justification, enter the estimated total for the preliminary costs.
Total for preliminary costs |  |  |  | 0

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only