## Sheet1
NIAGARA POINT NAME | DESCRIPTIVE NAME | PRECISION | FACETS (UNIT) | Trend | Alarm Priority | Alarm | Analytic Tags
ahu##DischargeTemp | AHU Discharge Temperature (for VAV boxes) | 1 | fahrenheit | X | Low | X
airPressure | Pneumatic Air Pressure | 1 | psi | X | Med | X
airPressureSp | Pneumatic Air Pressure Setpoint | 1 | psi
batteryVoltage | Battery Voltage | 1 | V | X | Low | X
Boiler | Boiler Command | n/a | On/Off
boilerAlarm | Boiler Alarm | n/a | Alarm/Normal |  | High | X
boilerDemand | Boiler Percent of Maximum Output (firing rate) | 0 | percent
boilerEfficiency | Boiler Efficiency of Combustion | 1 | percent
boilerFlameFailAlarm | Boiler Flame Alarm | n/a | Alarm/Normal |  | High | X
boilerLoad | Boiler Actual Energy Production | 0 | percent
boilerOvr | Boiler Override Command | n/a | On/Off
boilerStatus | Boiler Status | n/a | On/Off | X | Med | X
buildingPressure | Building Pressure | 2 | inches_of_water | X
buildingPressureSp | Building Pressure Setpoint | 2 | inches_of_water
bypassDamper | Bypass Damper Command | 0 | percent | X
bypassDamperFb | Bypass Damper Feedback | 0 | percent
bypassDamperOvr | Bypass Damper Override Command | 0 | percent
bypassValve | Bypass Valve | 0 | percent | X
bypassValveFb | Bypass Valve Feedback | 0 | percent
bypassValveOvr | Bypass Valve Override | 0 | percent
chiller | Chiller Command | n/a | On/Off | X |  |  | a:chillerCmd
chillerAlarm | Chiller Alarm | n/a | Alarm/Normal |  | Med | X
chillerDemandHiSp | Chiller Output Maximum Value | 0 | percent
chillerEfficiency | Chiller Efficiency of Refrigeration | 1 | percent
chillerLoad | Chiller Actual Energy Production | 0 | percent
chillerOvr | Chiller Override Command | n/a | On/Off
chillerStatus | Chiller Status | n/a | On/Off | X | Low | X | a:chillerStatus
circPumpXXX | Circulation Pump Command | n/a | On/Off
circPumpXXXAlarm | Circulation Pump Alarm | n/a | Alarm/Normal |  | Low | X
circPumpXXXBypass | Circulation Pump Bypass | n/a | Bypass/Normal
circPumpXXXCurrent | Circulation Pump Current | 1 | A
circPumpXXXEnergy | Circulation Pump Energy | 1 | kWh
circPumpXXXEnteringPres sure | Circulation Pump Entering Pressure | 2 | psi | X
circPumpXXXFault | Circulation Pump Fault | n/a | Fault/Normal |  | Low | X
circPumpXXXFrequency | Circulation Pump Frequency | 1 | Hz
circPumpXXXLeavingPress ure | Circulation Pump Leaving Pressure | 2 | psi | X
circPumpXXXOvr | Circulation Pump Command Override | n/a | On/Off
circPumpXXXPowerReal | Circulation Pump Power Demand | 2 | kW
circPumpXXXSpeed | Circulation Pump Speed | 0 | percent | X
circPumpXXXSpeedFb | Circulation Pump Speed Feedback | 0 | percent
circPumpXXXSpeedOvr | Circulation Pump Speed Override | 0 | percent
circPumpXXXSpeedSp | Circulation Pump Speed Setpoint | 0 | percent
circPumpXXXStatus | Circulation Pump Status | n/a | On/Off | X | Low | X
circPumpXXXTorque | Circulation Pump Torque Percent of Maximum | 0 | percent
coldDeckDamper | Cold Deck Damper Command | 0 | percent | X
coldDeckDamperFb | Cold Deck Damper Feedback | 0 | percent
coldDeckDamperOvr | Cold Deck Damper Override Command | 0 | percent
coldDeckDischargeEnthalp y | Cold Deck Discharge Enthalpy | 1 | BTU/lb
coldDeckDischargeEnthalp ySp | Cold Deck Discharge Enthalpy Setpoint | 1 | BTU/lb
coldDeckDischargeFlow | Cold Deck Discharge Flow | 0 | cfm | X
coldDeckDischargeFlowSp | Cold Deck Discharge Flow Setpoint | 0 | cfm
coldDeckDischargeHumidit y | Cold Deck Discharge Humidity | 1 | percent_relative_humidity | X
coldDeckDischargeHumidit ySp | Cold Deck Discharge Humidity Setpoint | 1 | percent_relative_humidity
coldDeckDischargePressur e | Cold Deck Discharge Pressure | 2 | inches_of_water | X
coldDeckDischargePressur eSp | Cold Deck Discharge Pressure Setpoint | 2 | inches_of_water
coldDeckDischargeTemp | Cold Deck Discharge Temperature | 1 | fahrenheit | X
coldDeckDischargeTempSp | Cold Deck Discharge Temperature Setpoint | 1 | fahrenheit
coldDeckFan | Cold Deck Fan Command | n/a | On/Off
coldDeckFanAlarm | Cold Deck Fan Alarm | n/a | On/Off |  | Med | X
coldDeckFanBypass | Cold Deck Fan Bypass | n/a | Bypass/Normal
coldDeckFanCurrent | Cold Deck Fan Current | 1 | A
coldDeckFanDCVoltage | Cold Deck Fan DC Voltage | 1 | V
coldDeckFanEnergy | Cold Deck Fan Energy | 1 | kWh
coldDeckFanEnteringPress ure | Cold Deck Fan Entering Pressure | 2 | inches_of_water | X
coldDeckFanFault | Cold Deck Fan Fault | n/a | Fault/Normal |  | Low | X
coldDeckFanFrequency | Cold Deck Fan Frequency | 1 | Hz
coldDeckFanHandMode | Cold Deck Fan Hand/Auto Mode | n/a | Hand/Auto
coldDeckFanLeavingPress ure | Cold Deck Fan Leaving Pressure | 2 | inches_of_water | X
coldDeckFanMotorSpeed | Cold Deck Fan Motor Speed | 0 | rpm
coldDeckFanMotorTemp | Cold Deck Fan Motor Temperature | 1 | Hand/Auto
coldDeckFanOvr | Cold Deck Fan Override Command | n/a | On/Off
coldDeckFanPowerReal | Cold Deck Fan Power Demand | 1 | kW
coldDeckFanPressureHiAla rm | Cold Deck Fan High Pressure Alarm | n/a | Alarm/Normal | X | High | X
coldDeckFanPressureLoAla rm | Cold Deck Fan Low Pressure Alarm | n/a | Alarm/Normal | X | High | X
coldDeckFanSpeed | Cold Deck Fan Speed | 1 | percent | X
coldDeckFanSpeedFb | Cold Deck Fan Speed Feedback | 1 | percent
coldDeckFanSpeedOvr | Cold Deck Fan Speed Override Command | 1 | percent
coldDeckFanSpeedSp | Cold Deck Fan Speed Setpoint | 1 | percent
coldDeckFanStatus | Cold Deck Fan Status | n/a | On/Off | X | Low | X
coldDeckFanTorque | Cold Deck Fan Torque Percent of Maximum | 1 | percent
coldDeckFanVoltage | Cold Deck Fan Voltage | 1 | V
condEnteringFlow | Condenser Entering Flow | 0 | gal/min | X
condEnteringFlowSp | Condenser Entering Flow Setpoint | 0 | gal/min
condEnteringFlowTotal | Condenser Entering Flow Total | 0 | gal/min | X
condEnteringPressure | Condenser Entering Pressure | 2 | psi | X
condEnteringTemp | Condenser Entering Temperature | 1 | fahrenheit | X
condEnteringTempSp | Condenser Entering Temperature Setpoint | 1 | fahrenheit
condFlowStatus | Condenser Flow Status | n/a | Flow/No Flow | X | Low | X
condIsoValve | Condenser Isolation Valve Command | n/a | Open/Closed
condIsoValveOvr | Condenser Isolation Valve Command Override | n/a | Open/Closed
condIsoValveStatus | Condenser Isolation Valve Status | n/a | Open/Closed | X
condLeavingFlow | Condenser Leaving Flow | 0 | gal/min | X
condLeavingFlowSp | Condenser Leaving Flow Setpoint | 0 | gal/min
condLeavingFlowMinSp | Condenser Leaving Flow Minimum Setpoint | 0 | gal/min
condLeavingFlowMaxSp | Condenser Leaving Flow Maximum Setpoint | 0 | gal/min
condLeavingFlowTotal | Condenser Leaving Flow Total | 0 | gal/min | X
condLeavingPressure | Condenser Leaving Pressure | 2 | psi | X
condLeavingTemp | Condenser Leaving Temperature | 1 | fahrenheit | X
condLeavingTempSp | Condenser Leaving Temperature Setpoint | 1 | fahrenheit
condPressureDelta | Condenser Pressure Differential | 2 | psi | X
condPressureDeltaSp | Condenser Pressure Differential Setpoint | 2 | psi
condPumpXXX | Condenser Pump Command | n/a | On/Off
condPumpXXXAlarm | Condenser Pump Alarm | n/a | Alarm/Normal | X | Med | X
condPumpXXXBypass | Condenser Pump Bypass | n/a | Bypass/Normal
condPumpXXXCurrent | Condenser Pump Current | 1 | A
condPumpXXXDCVoltage | Condenser Pump DC Voltage | 1 | V
condPumpXXXEnergy | Condenser Pump Energy | 1 | kWh
condPumpXXXEnteringPre ssure | Condenser Pump Entering Pressure | 2 | psi | X
condPumpXXXFault | Condenser Pump Fault | n/a | Fault/Normal | X | Med | X
condPumpXXXFrequency | Condenser Pump Frequency | 1 | Hz
condPumpXXXLeavingPres sure | Condenser Pump Leaving Pressure | 2 | psi | X
condPumpXXXOvr | Condenser Pump Command Override | n/a | On/Off
condPumpXXXPowerReal | Condenser Pump Power Demand | 2 | kW
condPumpXXXSpeed | Condenser Pump Speed | 0 | percent | X
condPumpXXXSpeedFb | Condenser Pump Speed Feedback | 0 | percent
condPumpXXXSpeedOvr | Condenser Pump Speed Override | 0 | percent
condPumpXXXSpeedSp | Condenser Pump Speed Setpoint | 0 | percent
condPumpXXXStatus | Condenser Pump Status | n/a | On/Off | X | Low | X
condPumpXXXTorque | Condenser Pump Torque Percent of Maximum | 0 | percent
condTempDelta | Condenser Temperature Delta | 1 | fahrenheit | X
coolantLevel | Coolant Level | 1 | percent | X | High | X
coolantTemp | Coolant Temperature | 1 | fahrenheit | X | High | X
coolingCoilDischargeTemp | Cooling Coil Discharge Temperature | 1 | fahrenheit | X
coolingCoilDischargeTemp Sp | Cooling Coil Discharge Temperature Setpoint | 1 | fahrenheit
coolingCoilEnergy | Cooling Coil Energy (Tons Refrig) | 0 | tonrefh
coolingCoilEnteringFlow | Cooling Coil Entering Flow | 0 | gal/min | X
coolingCoilEnteringTemp | Cooling Coil Entering Temperature | 1 | fahrenheit | X
coolingCoilLeavingTemp | Cooling Coil Leaving Temperature | 1 | fahrenheit | X
coolingCoilPump | Cooling Coil Pump Command | n/a | On/Off
coolingCoilPumpCurrent | Cooling Coil Pump Current | 1 | A
coolingCoilPumpOvr | Cooling Coil Pump Override Command | n/a | On/Off
coolingCoilPumpPowerReal | Cooling Coil Pump Power Demand | 1 | kW
coolingCoilPumpStatus | Cooling Coil Pump Status | n/a | On/Off | X | Low | X
coolingDemand | Cooling Demand | 0 | percent |  |  |  | a:coolingValvePos
coolingEnable | Cooling Enable Command (Lockout) | n/a | Available/Unavailable
coolingEnableSp | Cooling Enable Setpoint (Lockout) | 1 | fahrenheit
coolingStageMinOffSp | Cooling Stage Minimum Off Time Setpoint | 0 | seconds
coolingStageMinOnSp | Cooling Stage Minimum On Time Setpoint | 0 | seconds
coolingStageXX | Cooling Stage XX Command | n/a | On/Off
coolingStageXXOvr | Cooling Stage XX Override Command | n/a | On/Off
coolingStageXXStatus | Cooling Stage XX Status | n/a | On/Off | X | Low | X
coolingValve | Cooling Valve Command | 0 | percent |  |  |  | a:coolingValveCmd
coolingValveFb | Cooling Valve Feedback | 0 | percent |  |  |  | a:coolingValvePos
coolingValveOvr | Cooling Valve Override Command | 0 | percent
coolingValveOneThird | Cooling Valve 1/3 Command | 0 | percent
coolingValveOneThirdFb | Cooling Valve 1/3 Status | 0 | percent | X
coolingValveOneThirdOvr | Cooling Valve 1/3 Override Command | 0 | percent
coolingValveTwoThird | Cooling Valve 2/3 Command | 0 | percent
coolingValveTwoThirdFb | Cooling Valve 2/3 Status | 0 | percent | X
coolingValveTwoThirdOvr | Cooling Valve 2/3 Override Command | 0 | percent
current | Current Average | 1 | A | X
currentPhaseA | Current (Phase A) | 1 | A | X
currentPhaseB | Current (Phase B) | 1 | A | X
currentPhaseC | Current (Phase C) | 1 | A | X
daytimeWarmUp | Daytime Warm Up Command | n/a | On/Off
daytimeWarmUpSp | Daytime Warm Up Setpoint | 1 | fahrenheit
decouplerFlow | Decoupler Water Flow | 1 | gal/min | X
decouplerTemp | Decoupler Water Temperature | 1 | fahrenheit | X
dehumidEnable | Dehumidification Enable Command (Lockout) | n/a | On/Off
dehumidSp | Dehumidification Setpoint | 1 | percent_relative_humidity
dischargeDamper | Discharge Damper Command | 0 | percent | X |  |  | a:spaceDamperPos (For VAVs)
dischargeDamperFb | Discharge Damper Feedback | 0 | percent
dischargeDamperOvr | Discharge Damper Command Override | 0 | percent
dischargeDewpoint | Discharge Dewpoint | 1 | fahrenheit | X
dischargeEnthalpy | Discharge Enthalpy | 1 | BTU/lb | X
dischargeEnthalpySp | Discharge Enthalpy Setpoint | 1 | BTU/lb
dischargeFan | Discharge Fan Command | n/a | On/Off |  |  |  | a:supplyFanCmd
dischargeFanAlarm | Discharge Fan Alarm | n/a | Alarm/Normal | X | Med | X
dischargeFanBypass | Discharge Fan Bypass | n/a | Bypass/Normal
dischargeFanCurrent | Discharge Fan Current | 1 | A
dischargeFanDCVoltage | Discharge Fan DC Voltage | 1 | V
dischargeFanEnergy | Discharge Fan Energy | 1 | kWh
dischargeFanEnteringPress ure | Discharge Fan Entering Pressure | 2 | inches_of_water | X
dischargeFanFault | Discharge Fan Fault | n/a | Fault/Normal | X | Med | X
dischargeFanFrequency | Discharge Fan Frequency | 1 | Hz
dischargeFanHandMode | Discharge Fan Hand/Auto Mode | n/a | Hand/Auto
dischargeFanLeavingPress ure | Discharge Fan Leaving Pressure | 2 | inches_of_water | X
dischargeFanMotorSpeed | Discharge Fan Motor Speed | 0 | rpm
dischargeFanMotorTemp | Discharge Fan Motor Temperature | 1 | fahrenheit
dischargeFanOvr | Discharge Fan Override Command | n/a | On/Off
dischargeFanPowerReal | Discharge Fan Power Demand | 1 | kW
dischargeFanPressureHiAl arm | Discharge Fan High Pressure Alarm | n/a | Alarm/Normal | X | High | X
dischargeFanPressureLoAl arm | Discharge Fan Low Pressure Alarm | n/a | Alarm/Normal | X | High | X
dischargeFanSpeed | Discharge Fan Speed | 1 | percent | X
dischargeFanSpeedFb | Discharge Fan Speed Feedback | 1 | percent
dischargeFanSpeedOvr | Discharge Fan Speed Override Command | 1 | percent
dischargeFanSpeedSp | Discharge Fan Speed Setpoint | 1 | percent
dischargeFanStatus | Discharge Fan Status | n/a | On/Off | X | High | X | a:supplyFanStatus
dischargeFanTorque | Discharge Fan Torque Percent of Maximum | 1 | percent
dischargeFanVoltage | Discharge Fan Voltage | 1 | V
dischargeFlow | Discharge Flow | 0 | cfm | X |  |  | a:spaceSupplyAirFlow (For VAVs)
dischargeFlowMinSp | VAV Air Flow Min Setpoint | 1 | cfm
dischargeFlowMaxSp | VAV Air Flow Max Setpoint | 1 | cfm
dischargeFlowCoolMaxSp | Discharge Flow Cool Max Setpoint | 0 | cfm |  |  |  | a:spaceSupplyAirFlowMaxSp (For VAVs)
dischargeFlowCoolMinSp | Discharge Flow Cool Min Setpoint | 0 | cfm |  |  |  | a:spaceSupplyAirFlowMinSp (For VAVs)
dischargeFlowHeatSp | Discharge Flow Heat Setpoint | 0 | cfm
dischargeFlowSp | Discharge Flow Setpoint | 0 | cfm | X |  |  | a:spaceSupplyAirFlowSp (For VAVs)
dischargeFlowStandbySp | Discharge Flow Cool Standby Setpoint | 0 | cfm
dischargeHumidity | Discharge Humidity | 1 | percent_relative_humidity | X
dischargeHumiditySp | Discharge Humidity Setpoint | 1 | percent_relative_humidity
dischargeHumidityHiLimitS p | Discharge Humidity High Limit Setpoint | 1 | percent_relative_humidity
dischargeIsoDamper | Discharge Isolation Damper Command | n/a | Open/Closed | X
dischargeIsoDamperOvr | Discharge Isolation Damper Override Command | n/a | Open/Closed
dischargeIsoDamperStatus | Discharge Isolation Damper Status | n/a | Open/Closed | X
dischargePressure | Discharge Pressure | 2 | inches_of_water | X |  |  | a:supplyAirStaticPressure
dischargePressureHiAlarm | Discharge Pressure High Alarm | n/a | Alarm/Normal | X | High | X
dischargePressureLoAlarm | Discharge Pressure Low Alarm | n/a | Alarm/Normal | X | High | X
dischargePressureMaxSp | Discharge Pressure Maximum Setpoint | 2 | inches_of_water
dischargePressureMinSp | Discharge Pressure Minimum Setpoint | 2 | inches_of_water
dischargePressureSp | Discharge Pressure Setpoint | 2 | inches_of_water |  |  |  | a:supplyAirStaticPressureSp
dischargeSmoke | Discharge Smoke Alarm | n/a | Alarm/Normal | X | High | X
dischargeTemp | Discharge Temperature | 1 | fahrenheit | X |  |  | a:supplyAirTemp OR a:spaceSupplyAirTemp ( For VAVs )
dischargeTempCoolSp | Discharge Temperature Cooling Setpoint | 1 | fahrenheit
dischargeTempHeatSp | Discharge Temperature Heating | 1 | fahrenheit
dischargeTempMaxSp | Discharge Temperature Max Setpoint (Reset) | 1 | fahrenheit
dischargeTempMinSp | Discharge Temperature Min Setpoint (Reset) | 1 | fahrenheit
dischargeTempSp | Discharge Temperature Setpoint | 1 | fahrenheit |  |  |  | a:supplyAirTempSp
dischargeVelocity | Discharge Velocity | 2 | ft/min | X
dischargeVelocityPressure | Discharge Velocity Pressure | 2 | inches_of_water | X
divertingValve | Diverting Valve Command | 0 | percent
divertingValveOvr | Diverting Valve Command Override | 0 | percent
divertingValveFb | Diverting Valve Feedback | 0 | percent
drainValve | Drain Valve (for sump) | n/a | Open/Closed | X
econEnable | Economizer Enable Command (Lockout) | n/a | Available/Unavailable |  |  |  | a:economizerStatus
econEnableEnthalpySp | Economizer Enable Enthalpy Setpoint | 1 | BTU/lb
econEnableSp | Economizer Enable Temperature Setpoint | 1 | fahrenheit |  |  |  | a:economizerSp
energy | Energy (Uses/makes power) | 1 | kWh | X
engineFuelLevel | Engine Fuel Level | 1 | percent
equipDescription | Equipment Description (ie: McQuay 4DX 2GH) | n/a
equipName | Equipment Display Name (ie: AHUFitnessRM) | n/a
equipServedBy | Equipment Served By (ie: AHUFitnessRM) | n/a
equipServes | Equipment Served (ie: Open Office 123) | n/a
equipSite | Equipment Site Name | n/a
equipStatLocation | Equipment Sensor Location | n/a
equipTag | Equipment Name that is 'Short' | n/a
evapEnteringFlow | Evaporator Entering Flow | 0 | gal/min | X
evapEnteringFlowSp | Evaporator Entering Flow Setpoint | 0 | gal/min
evapEnteringPressure | Evaporator Entering Pressure | 2 | psi | X
evapEnteringTemp | Evaporator Entering Temperature | 1 | fahrenheit | X
evapFlowStatus | Evaporator Flow Status | n/a | Flow/No Flow | X | Low | X
evapIsoValve | Evaporator Isolation Valve Command | n/a | Open/Closed
evapIsoValveOvr | Evaporator Isolation Valve Command Override | n/a | Open/Closed
evapIsoValveStatus | Evaporator Isolation Valve Status | n/a | Open/Closed | X
evapLeavingFlow | Evaporator Leaving Flow | 0 | gal/min | X
evapLeavingFlowSp | Evaporator Leaving Flow Setpoint | 0 | gal/min
evapLeavingFlowMinSp | Evaporator Leaving Flow Minimum Setpoint | 0 | gal/min
evapLeavingFlowMaxSp | Evaporator Leaving Flow Maximum Setpoint | 0 | gal/min
evapLeavingPressure | Evaporator Leaving Pressure | 0 | inches_of_water | X
evapLeavingTemp | Evaporator Leaving Temperature | 1 | fahrenheit | X
evapLeavingTempSp | Evaporator Leaving Temperature Setpoint | 1 | fahrenheit
evapPressureDelta | Evaporator Pressure Differential | 2 | psi | X
evapPressureDeltaSp | Evaporator Pressure Differential Setpoint | 2 | psi
evapPumpXXX | Evaporator Pump Command | n/a | On/Off
evapPumpXXXAlarm | Evaporator Pump Alarm | n/a | Alarm/Normal | X | Med | X
evapPumpXXXBypass | Evaporator Pump Bypass | n/a | Bypass/Normal
evapPumpXXXCurrent | Evaporator Pump Current | 1 | A
evapPumpXXXEnergy | Evaporator Pump Energy | 1 | kWh
evapPumpXXXEnteringPre ssure | Evaporator Pump Entering Pressure | 2 | psi | X
evapPumpXXXFault | Evaporator Pump Fault | n/a | Fault/Normal | X | Med | X
evapPumpXXXFrequency | Evaporator Pump Frequency | 1 | Hz
evapPumpXXXLeavingPres sure | Evaporator Pump Leaving Pressure | 2 | psi | X
evapPumpXXXOvr | Evaporator Pump Command Override | n/a | On/Off
evapPumpXXXPowerReal | Evaporator Pump Power Demand | 2 | kW
evapPumpXXXSpeed | Evaporator Pump Speed | 0 | percent | X
evapPumpXXXSpeedFb | Evaporator Pump Speed Feedback | 0 | percent
evapPumpXXXSpeedOvr | Evaporator Pump Speed Override | 0 | percent
evapPumpXXXSpeedSp | Evaporator Pump Speed Setpoint | 0 | percent
evapPumpXXXStatus | Evaporator Pump Status | n/a | On/Off | X | Low | X
evapPumpXXXTorque | Evaporator Pump Torque Percent of Maximum | 0 | percent
evapTempDelta | Evaportator Temperature Differential | 1 | fahrenheit | X
exhaustDamper | Exhaust Damper | 0 | percent | X
exhaustDamperFb | Exhaust Damper Feedback | 0 | percent
exhaustDamperOvr | Exhaust Fan Command Override | 1 | percent
exhaustFan | Exhaust Fan Command | n/a | On/Off | X
exhaustFanAlarm | Exhaust Fan Alarm | n/a | Alarm/Normal | X | Med | X
exhaustFanBypass | Exhaust Fan Bypass | n/a | Bypass/Normal
exhaustFanCurrent | Exhaust Fan Current | 1 | A
exhaustFanDCVoltage | Exhaust Fan DC Voltage | 1 | V
exhaustFanEnableSp | Outside Damper Position at which Exhaust is Enabled | 1 | percent | X
exhaustFanEnergy | Exhaust Fan Energy | 1 | kWh
exhaustFanEnteringPressur e | Exhaust Fan Entering Pressure | 2 | inches_of_water | X
exhaustFanFault | Exhaust Fan Fault | n/a | Fault/Normal | X | Med | X
exhaustFanFrequency | Exhaust Fan Frequency | 1 | Hz
exhaustFanHandMode | Exhaust Fan Hand/Auto Mode | n/a | Hand/Auto
exhaustFanLeavingPressur e | Exhaust Fan Leaving Pressure | 2 | inches_of_water | X
exhaustFanMotorSpeed | Exhaust Fan Motor Speed | 0 | percent | X
exhaustFanMotorTemp | Exhaust Fan Motor Temperature | 1 | fahrenheit
exhaustFanOvr | Exhaust Fan Command Override | n/a | On/Off
exhaustFanPowerReal | Exhaust Fan Power Demand | 1 | kW
exhaustFanPressureHiAlar m | Exhaust Fan High Pressure Alarm | n/a | Alarm/Normal | X | High | X
exhaustFanPressureLoAlar m | Exhaust Fan Low Pressure Alarm | n/a | Alarm/Normal | X | High | X
exhaustFanSpeed | Exhaust Fan Speed | 1 | percent | X
exhaustFanSpeedFb | Exhaust Fan Speed Feedback | 1 | percent
exhaustFanSpeedOvr | Exhaust Fan Speed Command Override | 1 | percent
exhaustFanSpeedSp | Exhaust Fan Speed Setpoint | 1 | percent
exhaustFanStatus | Exhaust Fan Status | n/a | On/Off | X | Low | X
exhaustFanTorque | Exhaust Fan Torque Percent of Maximum | 1 | percent
exhaustFanVoltage | Exhaust Fan Voltage | 1 | V
exhaustFlow | Exhaust Airflow | 0 | cfm | X
exhaustFlowSp | Exhaust Airflow Setpoint | 0 | cfm
exhaustHumidity | Exhaust Humidity | 1 | percent_relative_humidity | X
exhaustIsoDamper | Exhaust Isolation Damper | n/a | Open/Closed | X
exhaustIsoDamperFb | Exhaust Isolation Damper Feedback | 0 | percent
exhaustIsoDamperOvr | Exhaust Isolation Damper Command Override | n/a | Open/Closed
exhaustIsoDamperStatus | Exhaust Isolation Damper Status | n/a | Open/Closed
exhaustTemp | Exhaust Temperature | 1 | fahrenheit | X
faceDamper | Face Damper Command (% open to face) | 0 | percent
faceDamperEnable | Face Bypass Mode Enable | n/a | Available/Unavailable
faceDamperFb | Face Damper Feedback (% open to face) | 0 | percent | X
faceDamperOvr | Face Damper Command Override (% open to face) | 0 | percent
filterAlarm | Filter Status | n/a | Alarm/Normal | X | Low | X
filterPressureDelta | Filter Pressure Differential | 2 | inches_of_water | X | Low | X
finalFilterAlarm | Filter Final Status | n/a | Alarm/Normal | X | Low | X
finalFilterPressureDelta | Filter Final Pressure Differential | 2 | inches_of_water | X | Low | X
fireExtinguisherXXPressure | Fire Extinguisher Pressure | 2 | psi | X
fireExtinguisherXXStatus | Fire Extinguisher Status | n/a | Alarm/Normal | X | High | X
flow | Flow Rate | 0 | gal/min | X
flowTotal | Totalized Flow | 0 | gallons | X
frequency | Frequency | 1 | Hz | X
heatingCoilDischargeTemp | Heating Coil Discharge Temperature | 1 | fahrenheit | X
heatingCoilDischargeTemp Sp | Heating Coil Discharge Temperature Setpoint | 1 | fahrenheit
heatingCoilEnergy | Heating Coil Energy | 0 | kBTU/h
heatingCoilEnteringFlow | Heating Coil Entering Flow | 0 | gal/min | X
heatingCoilEnteringTemp | Heating Coil Entering Temperature | 1 | fahrenheit | X
heatingCoilLeavingTemp | Heating Coil Leaving Temperature | 1 | fahrenheit | X
heatingCoilPump | Heating Coil Pump Command | n/a | On/Off
heatingCoilPumpOvr | Heating Coil Pump Command Ovr | n/a | On/Off
heatingCoilPumpPowerRea l | Heating Coil Pump Demand | 1 | kW
heatingCoilPumpStatus | Heating Coil Pump Status | n/a | On/Off | X | Low | X
heatingDemand | Heating Demand | 0 | percent |  |  |  | a:heatingValvePos
heatingEnable | Heating Enable Command | n/a | Available/Unavailable |  |  |  | a:heatingHotWaterSystem
heatingEnableSp | Heating Enable Setpoint | 1 | fahrenheit
heatingStageMinOffSp | Heating Stage Minimum Off Time Setpoint | 0 | seconds
heatingStageMinOnSp | Heating Stage Minimum On Time Setpoint | 0 | seconds
heatingStageXX | Heating Stage XX Command | n/a | On/Off
heatingStageXXOvr | Heating Stage XX Command Override | n/a | On/Off
heatingStageXXStatus | Heating Stage XX Status | n/a | On/Off | X
heatingValve | Heating Valve Command | 0 | percent | X |  |  | a:heatingValveCmd OR a:spaceHeatingValvePos (For VAVs)
heatingValveFb | Heating Valve Feedback | 0 | percent
heatingValveOvr | Heating Valve Command Override | 0 | percent
heatingValveOneThird | Heating Valve 1/3 Command | 0 | percent
heatingValveOneThirdFb | Heating Valve 1/3 Status | 0 | percent | X
heatingValveOneThirdOvr | Heating Valve 1/3 Command Override | 0 | percent
heatingValveTwoThird | Heating Valve 2/3 Command | 0 | percent
heatingValveTwoThirdFb | Heating Valve 2/3 Status | 0 | percent | X
heatingValveTwoThirdOvr | Heating Valve 2/3 Command Override | 0 | percent
heatWheel | Heat Wheel Command | n/a | On/Off | X
heatWheelAlarm | Heat Wheel Alarm | n/a | Alarm/Normal | X | Med | X
heatWheelBypass | Heat Wheel Bypass | n/a | Bypass/Normal
heatWheelCurrent | Heat Wheel Current | 1 | A
heatWheelEnergy | Heat Wheel Energy | 1 | kWh
heatWheelFault | Heat Wheel Fault | n/a | Fault/Normal | X | Low | X
heatWheelFrequency | Heat Wheel Frequency | 1 | Hz
heatWheelOvr | Heat Wheel Command Override | n/a | On/Off
heatWheelPowerReal | Heat Wheel Demand | 1 | Hz | X
heatWheelSpeed | Heat Wheel Speed | 1 | percent | X
heatWheelSpeedFb | Heat Wheel Speed Feedback | 1 | percent
heatWheelSpeedOvr | Heat Wheel Speed Command Override | 1 | percent
heatWheelSpeedSp | Heat Wheel Speed Setpoint | 1 | percent
heatWheelStatus | Heat Wheel Status | n/a | On/Off | X
heatWheelTorque | Heat Wheel Torque Percent of Maximum | 1 | percent
heatWheelDischargeTemp | Heat Wheel Discharge Temperature | 1 | fahrenheit | X
heatWheelExhaustTemp | Heat Wheel Exhaust Temperature | 1 | fahrenheit | X
heatWheelOutsideTemp | Heat Wheel Outside Temperature | 1 | fahrenheit | X
heatWheelReturnTemp | Heat Wheel Return Temperature | 1 | fahrenheit | X
hotDeckDamper | Hot Deck Damper Command | 0 | percent | X
hotDeckDamperFb | Hot Deck Damper Feedback | 0 | percent
hotDeckDamperOvr | Hot Deck Damper Override | 0 | percent
hotDeckDischargeEnthalpy | Hot Deck Discharge Enthalpy | 1 | BTU/lb | X
hotDeckDischargeEnthalpy Sp | Hot Deck Discharge Enthalpy Setpoint | 1 | BTU/lb
hotDeckDischargeFlow | Hot Deck Discharge Airflow | 0 | cfm | X
hotDeckDischargeFlowSp | Hot Deck Discharge Airflow Setpoint | 0 | cfm
hotDeckDischargeHumidity | Hot Deck Discharge Humidity | 1 | percent_relative_humidity | X
hotDeckDischargeHumidity Sp | Hot Deck Discharge Humidity Setpoint | 1 | percent_relative_humidity
hotDeckDischargePressure | Hot Deck Discharge Pressure | 2 | inches_of_water | X
hotDeckDischargePressure Sp | Hot Deck Discharge Pressure Setpoint | 2 | inches_of_water
hotDeckDischargeTemp | Hot Deck Discharge Temperature | 1 | fahrenheit | X
hotDeckDischargeTempSp | Hot Deck Discharge Temperature Setpoint | 1 | fahrenheit
hotDeckFan | Hot Deck Fan Command | n/a | On/Off
hotDeckFanAlarm | Hot Deck Fan Alarm | n/a | Alarm/Normal | X | Med | X
hotDeckFanBypass | Hot Deck Fan Bypass | n/a | Bypass/Normal
hotDeckFanCurrent | Hot Deck Fan Current | 1 | A
hotDeckFanDCVoltage | hotDeck Fan DC Voltage | 1 | V
hotDeckFanEnergy | Hot Deck Fan Energy | 1 | kWh
hotDeckFanEnteringPressu re | Hot Deck Fan Entering Pressure | 2 | inches_of_water | X
hotDeckFanFault | Hot Deck Fan Fault | n/a | Fault/Normal | X | Med | X
hotDeckFanFrequency | Hot Deck Fan Frequency | 1 | Hz
hotDeckFanHandMode | hotDeck Fan Hand/Auto Mode | n/a | Hand/Auto
hotDeckFanLeavingPressur e | Hot Deck Fan Leaving Pressure | 2 | inches_of_water | X
hotDeckFanMotorSpeed | hotDeck Fan Motor Speed | 0 | percent
hotDeckFanMotorTemp | hotDeck Fan Motor Temperature | 1 | fahrenheit
hotDeckFanOvr | Hot Deck Fan Command Override | n/a | On/Off
hotDeckFanPowerReal | Hot Deck Fan Power Demand | 1 | kW
hotDeckFanPressureHiAlar m | Hot Deck Fan High Pressure Alarm | n/a | Alarm/Normal | X | High | X
hotDeckFanPressureLoAlar m | Hot Deck Fan Low Pressure Alarm | n/a | Alarm/Normal | X | High | X
hotDeckFanSpeed | Hot Deck Fan Speed | 1 | percent | X
hotDeckFanSpeedFb | Hot Deck Fan Speed Feedback | 1 | percent
hotDeckFanSpeedOvr | Hot Deck Fan Speed Command Override | 1 | percent
hotDeckFanSpeedSp | Hot Deck Fan Speed Setpoint | 1 | percent
hotDeckFanStatus | Hot Deck Fan Status | n/a | On/Off | X | Med | X
hotDeckFanTorque | Hot Deck Fan Torque Percent of Maximum | 1 | percent
hotDeckFanVoltage | hotDeck Fan Voltage | 1 | V
humidifier | Humidifier Command | n/a | On/Off
humidifierDemand | Humidifier Demand | 0 | percent | X
humidifierEnable | Humidifier Enable Command | n/a | Available/Unavailable
humidifierFault | Humidifier Fault | n/a | Fault/Normal | X | Low | X
humidifierIsoValve | Humidifier Isolation Valve Command | n/a | Open/Closed
humidifierIsoValveFb | Humidifier Isolation Valve Feedback | 0 | percent
humidifierIsoValveOvr | Humidifier Isolation Valve Command Override | n/a | Open/Closed
humidifierStatus | Humidifier Status | n/a | On/Off | X | Low | X
humidifierValve | Humidifier Valve Command | 1 | percent
humidifierValveFb | Humidifier Valve Feedback | 1 | percent
humidifierValveOvr | Humidifier Valve Command Override | 1 | percent
humidifierValveOneThird | Humidifier 1/3 Valve Command | 1 | percent | X
humidifierValveOneThirdFb | Humidifier 1/3 Valve Feedback | 1 | percent
humidifierValveOneThirdOv r | Humidifier 1/3 Valve Override Command | 1 | percent
humidifierValveTwoThird | Humidifier 2/3 Valve Command | 1 | percent | X
humidifierValveTwoThirdFb | Humidifier 2/3 Valve Feedback | 1 | percent
humidifierValveTwoThirdOv r | Humidifier 2/3 Valve Override Command | 1 | percent
intakeDamper | Intake Damper Command | 0 | percent | X
intakeDamperStatus | Intake Damper Status | n/a | Open/Closed
intakeDamperFb | Intake Damper Feedback | 0 | percent
intakeDamperOvr | Intake Damper Command Override | 0 | percent
intrusionAlarm | Intrusion Alarm | n/a | Alarm/Normal | X | High | X
intrusionArmed | Intrusion Armed | n/a | Armed/Disarmed | X | High | X
kFactor | Airflow Calibration Factor | 0 | unitless
lowLimitAlarm | Low Limit Thermostat | n/a | Alarm/Normal | X | High | X
makeupValve | Makeup Water Valve for Sump | n/a | Open/Closed | X | Med | X
meterStatus | Building Meters communcation status | n/a | Online/Offline | X | Low | X | a:meterHealth
minOutsideDamper | Minimum Outside Damper Command | 0 | percent | X
minOutsideDamperFb | Minimum Outside Damper Feedback | 0 | percent
minOutsideDamperOvr | Minimum Outside Damper Command Override | 0 | percent
minOutsideFan | Minimum Outside Fan Command | n/a | On/Off
minOutsideFanAlarm | Minimum Outside Fan Alarm | n/a | Alarm/Normal | X | Low | X
minOutsideFanBypass | Minimum Outside Fan Bypass | n/a | Bypass/Normal
minOutsideFanCurrent | Minimum Outside Fan Current | 1 | A
minOutsideFanDCVoltage | Minimum Outside Fan DC Voltage | 1 | V
minOutsideFanEnergy | Minimum Outside Fan Energy | 1 | kWh
minOutsideFanEnteringPre ssure | Minimum Outside Fan Entering Pressure | 2 | inches_of_water | X
minOutsideFanFault | Minimum Outside Fan Fault | n/a | Fault/Normal | X | Med | X
minOutsideFanFrequency | Minimum Outside Fan Frequency | 1 | Hz
minOutsideFanHandMode | Minimum Outside Fan Hand/Auto Mode | n/a | Hand/Auto
minOutsideFanLeavingPres sure | Minimum Outside Fan Leaving Pressure | 2 | inches_of_water | X
minOutsideFanMotorSpeed | Minimum Outside Fan Motor Speed | 0 | rpm
minOutsideFanMotorTemp | Minimum Outside Fan Motor Temperature | 1 | fahrenheit
minOutsideFanOvr | Minimum Outside Fan Override Command | n/a | On/Off
minOutsideFanPowerReal | Minimum Outside Fan Power Demand | 1 | kW
minOutsideFanPressureHiA larm | Minimum Outside Fan High Pressure Alarm | n/a | Alarm/Normal | X | High | X
minOutsideFanPressureLo Alarm | Minimum Outside Fan Low Pressure Alarm | n/a | Alarm/Normal | X | High | X
minOutsideFanSpeed | Minimum Outside Fan Speed | 1 | percent | X
minOutsideFanSpeedFb | Minimum Outside Fan Speed Feedback | 1 | percent
minOutsideFanSpeedOvr | Minimum Outside Fan Speed Override Command | 1 | percent
minOutsideFanSpeedSp | Minimum Outside Fan Speed Setpoint | 1 | percent
minOutsideFanStatus | Minimum Outside Fan Status | n/a | On/Off | X | Low | X
minOutsideFanTorque | Minimum Outside Fan Torque Percent of Maximum | 1 | percent
minOutsideFanVoltage | Minimum Outside Fan Voltage | 1 | V
minOutsideFilterAlarm | Minimum Outside Filter Alarm | n/a | Dirty/Clean | X | Low | X
minOutsideFilterPressureD elta | Minimum Outside Filter Pressure Delta | 2 | inches_of_water | X
mixedPressure | Mixed Pressure | 2 | inches_of_water | X
mixedPressureSp | Mixed Pressure Setpoint | 2 | inches_of_water
mixedTemp | Mixed Temperature | 1 | fahrenheit | X | High | X | hs:mixedAirTempSensor
mixedTempHiSp | Mixed Temperature High Setpoint | 1 | fahrenheit
mixedTempLoSp | Mixed Temperature Low Setpoint | 1 | fahrenheit
mixedTempSp | Mixed Temperature Setpoint | 1 | fahrenheit
mixingValve | Mixing Valve Command | 0 | percent | X
mixingValveFb | Mixing Valve Feedback | 0 | percent
mixingValveOvr | Mixing Valve Command Override | 0 | percent
morningCoolDown | Morning Cool Down Command | n/a | On/Off
morningFreeCooling | Morning Free Cooling Command | n/a | On/Off
morningWarmUp | Morning Warm Up Command | n/a | On/Off
morningWarmUpSp | Morning Warm Up Setpoint | 1 | fahrenheit
nightSetbackMode | Nigt Set Back Mode | n/a | On/Off
nightSetupMode | Unoccupied Cooling Mode | n/a | On/Off
occupancyMode | Occupied Mode | n/a | Occupied/Unoccupied |  |  |  | hs: occupied
occupancySensor | Occupancy Sensor | n/a | Occupied/Unoccupied
occupiedCoolSp | Occupied Cool Setpoint | 1 | fahrenheit
occupiedHeatSp | Occupied Heat Setpoint | 1 | fahrenheit
oilPressure | Oil Pressure | 2 | psi | X
oilTemp | Oil Temperature | 2 | psi | X
optimalStartMode | Optimal Start Mode | n/a | On/Off
optimalStopMode | Optimal Stop Mode | n/a | On/Off
outsideCO2 | Outside CO2 | 0 | ppm | X
outsideDamper | Outside Damper | 0 | percent | X |  |  | a:outsideAirDamperPos
outsideDamperFb | Outside Damper Feedback | 0 | percent
outsideDamperMinSp | Outside Damper Minimum Setpoint | 0 | percent
outsideDamperPos | Outside Damper Position | 0.1 | percent | X |  |  | a:outsideAirDamperPos
outsideDamperOvr | Outside Damper Command Override | 0 | percent
outsideDewpoint | Outside Dewpoint | 1 | fahrenheit | X
outsideEnthalpy | Outside Enthalpy | 1 | BTU/lb | X |  |  | a:outsideAirEnthalpy
outsideFan | Outside Fan Command | n/a | On/Off | X
outsideFanAlarm | Outside Fan Alarm | n/a | Alarm/Normal | X | Med | X
outsideFanBypass | Outside Fan Bypass | n/a | Bypass/Normal
outsideFanCurrent | Outside Fan Current | 1 | A
outsideFanDCVoltage | Outside Fan DC Voltage | 1 | V
outsideFanEnergy | Outside Fan Energy | 1 | kWh
outsideFanEnteringPressur e | Outside Fan Entering Pressure | 2 | inches_of_water | X
outsideFanFault | Outside Fan Fault | n/a | Fault/Normal | X | Med | X
outsideFanFrequency | Outside Fan Frequency | 1 | Hz
outsideFanHandMode | Outside Fan Hand/Auto Mode | n/a | Hand/Auto
outsideFanLeavingPressur e | Outside Fan Leaving Pressure | 2 | inches_of_water | X
outsideFanMotorSpeed | Outside Fan Motor Speed | 0 | rpm | X
outsideFanMotorTemp | Outside Fan Motor Temperature | 1 | fahrenheit
outsideFanOvr | Outside Fan Command Override | n/a | On/Off
outsideFanPowerReal | Outside Fan Power Demand | 1 | kW
outsideFanPressureHiAlar m | Outside Fan High Pressure Alarm | n/a | Alarm/Normal | X | High | X
outsideFanPressureLoAlar m | Outside Fan Low Pressure Alarm | n/a | Alarm/Normal | X | High | X
outsideFanSpeed | Outside Fan Speed | 1 | percent | X
outsideFanSpeedFb | Outside Fan Speed Feedback | 1 | percent
outsideFanSpeedOvr | Outside Fan Speed Command Override | 1 | percent
outsideFanSpeedSp | Outside Fan Speed Setpoint | 1 | percent
outsideFanStatus | Outside Fan Status | n/a | On/Off | X | Med | X
outsideFanTorque | Outside Fan Torque Percent of Maximum | 1 | percent
outsideFanVoltage | Outside Fan Voltage | 1 | V
outsideFilterAlarm | Outside Filter Alarm Status | n/a | On/Off | X | Low | X
outsideFilterPressureDelta | Outside Filter Pressure Delta | n/a | On/Off | X | Low | X
outsideFlow | Outside Airflow | 0 | cfm | X
outsideFlowMinSp | Outside Airflow Minimum Setpoint | 0 | cfm
outsideFlowSp | Outside Airflow Setpoint | 0 | cfm
outsideHumidity | Outside Humidity | 1 | percent_relative_humidity | X
outsideIsoDamper | Outside Isolation Damper | n/a | Open/Closed
outsideIsoDamperStatus | Outside Isolation Damper Status | n/a | Open/Closed
outsideIsoDamperOvr | Outside Isolation Damper Command Override | n/a | Open/Closed
outsideLightLevel | Outside Light Level | 0 | percent | X
outsidePressure | Outside Pressure | 2 | inches_of_water | X
outsideTemp | Outside Temperature | 1 | fahrenheit | X |  |  | a:outsideAirTemp
outsideVelocityPressure | Outside Velocity Pressure | 1 | FPM | X
outsideWindDegrees | Outside Wind Direction | n/a | N,S,E,W, Various | X
outsideWindSpeed | Outside Wind Speed | 1 | mph | X
perimeterHeatingValve | Perimeter Heating Valve Command | 0 | percent | X
perimeterHeatingValveFb | Perimeter Heating Valve Feedback | 0 | percent
perimeterHeatingValveOvr | Perimeter Heating Valve Command Override | 0 | percent
phaseLoss | Phase Loss Detector Input | n/a | Alarm/Normal | X | High | X
points | w/ % facet | 1 | percent |  |  |  | a:percent
powerApparent | Apparent Power (Total) | 1 | kVA | X
powerApparentPhaseA | Apparent Power (Phase A) | 1 | kVA
powerApparentPhaseB | Apparent Power (Phase B) | 1 | kVA
powerApparentPhaseC | Apparent Power (Phase C) | 1 | kVA
powerFactor | Power Factor | 2 | pf | X
powerFactorPhaseA | Power Factor (Phase A) | 2 | pf
powerFactorPhaseB | Power Factor (Phase B) | 2 | pf
powerFactorPhaseC | Power Factor (Phase C) | 2 | pf
powerReactive | Reactive Power (Total) | 1 | kVAR
powerReactivePhaseA | Reactive Power (Phase A) | 1 | kVAR
powerReactivePhaseB | Reactive Power (Phase B) | 1 | kVAR
powerReactivePhaseC | Reactive Power (Phase C) | 1 | kVAR
powerReal | Real Power (Total) | 1 | kW | X |  |  | a:powerDemand
powerRealPhaseA | Real Power (Phase A) | 1 | kW | X
powerRealPhaseB | Real Power (Phase B) | 1 | kW | X
powerRealPhaseC | Real Power (Phase C) | 1 | kW | X
preCoolingTemp | Pre-Cooling Temperature | 1 | fahrenheit | X
preCoolingTempSp | Pre-Cooling Temperature Setpoint | 1 | fahrenheit
preCoolingValve | Pre-Cooling Valve Command | 0 | percent | X
preCoolingValveFb | Pre-Cooling Valve Feedback | 0 | percent
preCoolingValveOvr | Pre-Cooling Valve Override Command | 0 | percent
preFilterAlarm | Filter Pre Status | n/a | Dirty/Clean | X | Low | X
preFilterPressureDelta | Filter Pre Pressure Differential | 2 | inches_of_water | X | Low | X
preHeatingTemp | Pre-Heating Temperature | 1 | fahrenheit | X
preHeatingTempHiSp | Pre-Heating High Temperature Setpoint | 1 | fahrenheit
preHeatingTempLoSp | Pre-Heating Low Temperature Setpoint | 1 | fahrenheit
preHeatingTempSp | Pre-Heating Temperature Setpoint | 1 | fahrenheit
preHeatingValve | Pre-Heating Valve Command | 0 | percent | X
preHeatingValveFb | Pre-Heating Valve Feedback | 0 | percent
preHeatingValveOvr | Pre-Heating Valve Command Override | 0 | percent
priEnteringFlow | Primary Entering Flow | 0 | gal/min | X
priEnteringFlowSp | Primary Entering Flow Setpoint | 0 | gal/min
priEnteringPressure | Primary Entering Pressure | 2 | psi | X
priEnteringTemp | Primary Entering Temperature | 1 | fahrenheit | X
priLeavingFlow | Primary Leaving Flow | 0 | gal/min | X
priLeavingFlowSp | Primary Leaving Flow Setpoint | 0 | gal/min
priLeavingPressure | Primary Leaving Pressure | 2 | psi | X
priLeavingTemp | Primary Leaving Temperature | 1 | fahrenheit | X
priLeavingTempSp | Primary Leaving Temperature Setpoint | 1 | fahrenheit
priPressureDelta | Primary Pressure Delta | 2 | psi | X
priPressureDeltaSp | Primary Pressure Delta Setpoint | 2 | psi
priPumpXXX | Primary Pump Command | n/a | On/Off
priPumpXXXAlarm | Primary Pump Alarm | n/a | Alarm/Normal | X | Med | X
priPumpXXXBypass | Primary Pump Bypass | n/a | Bypass/Normal
priPumpXXXEnergy | Primary Pump Energy | 1 | kWh
priPumpXXXCurrent | Primary Pump Current | 1 | A
priPumpXXXEnteringPress ure | Primary Pump Entering Pressure | 2 | psi | X
priPumpXXXFault | Primary Pump Fault | n/a | Fault/Normal | X | Med | X
priPumpXXXFrequency | Primary Pump Frequency | 1 | Hz
priPumpXXXLeavingPressu re | Primary Pump Leaving Pressure | 2 | psi | X
priPumpXXXOvr | Primary Pump Command Override | n/a | On/Off
priPumpXXXPowerReal | Primary Pump Power Demand | 2 | kW
priPumpXXXSpeed | Primary Pump Speed | 0 | percent | X
priPumpXXXSpeedFb | Primary Pump Speed Feedback | 0 | percent
priPumpXXXSpeedOvr | Primary Pump Speed Override | 0 | percent
priPumpXXXSpeedSp | Primary Pump Speed Setpoint | 0 | percent
priPumpXXXStatus | Primary Pump Status | n/a | On/Off | X | Med | X
priPumpXXXTorque | Primary Pump Torque Percent of Maximum | 0 | percent
priTempDelta | Primary Temperature Delta | 1 | fahrenheit | X
priTempDeltaSp | Primary Temperature Delta Setpoint | 1 | fahrenheit
pumpXXX | Primary Pump Command | n/a | On/Off
pumpXXXAlarm | Primary Pump Alarm | n/a | Alarm/Normal | X | Med | X
pumpXXXBypass | Primary Pump Bypass | n/a | Bypass/Normal
pumpXXXEnergy | Primary Pump Energy | 1 | kWh
pumpXXXCurrent | Primary Pump Current | 1 | A
pumpXXXEnteringPressure | Primary Pump Entering Pressure | 2 | psi | X
pumpXXXFault | Primary Pump Fault | n/a | Fault/Normal | X | Med | X
pumpXXXFrequency | Primary Pump Frequency | 1 | Hz
pumpXXXLeavingPressure | Primary Pump Leaving Pressure | 2 | psi | X
pumpXXXOvr | Primary Pump Command Override | n/a | On/Off
pumpXXXPowerReal | Primary Pump Power Demand | 2 | kW
pumpXXXSpeed | Primary Pump Speed | 0 | percent | X
pumpXXXSpeedFb | Primary Pump Speed Feedback | 0 | percent
pumpXXXSpeedOvr | Primary Pump Speed Override | 0 | percent
pumpXXXSpeedSp | Primary Pump Speed Setpoint | 0 | percent
pumpXXXStatus | Primary Pump Status | n/a | On/Off | X | Med | X
pumpXXXTorque | Primary Pump Torque Percent of Maximum | 0 | percent
reHeatingStageXX | Re-Heating Stage XX Command | n/a | On/Off | X
reHeatingStageXXOvr | Re-Heating Stage XX Command Override | n/a | On/Off
reHeatingStageXXStatus | Re-Heating Stage XX Status | n/a | On/Off | X
reHeatingValve | Re-Heating Valve Command | 0 | percent | X
reHeatingValveFb | Re-Heating Valve Feedback | 0 | percent
reHeatingValveOvr | Re-Heating Valve Command Override | 0 | percent
reliefDamper | Relief Damper Command | 0 | percent | X
reliefDamperStatus | Relief Damper Status | n/a | Open/Closed
reliefDamperFb | Relief Damper Feedback | 0 | percent | X
reliefDamperOvr | Relief Damper Command Override | 0 | percent
returnFlow | Return Air Flow | 0.1 | CFM |  |  |  | a:returnAirFlow
returnCO2 | Return CO2 | 0 | ppm | X |  |  | hs:returnAirCo2Sensor
returnCO2Sp | Return CO2 Setpoint | 0 | ppm
returnDamper | Return Damper | 0 | percent | X
returnDamperFb | Return Damper Feedback | 0 | percent
returnDamperOvr | Return Damper Command Override | 0 | percent
returnEnthalpy | Return Enthalpy | 1 | BTU/lb | X |  |  | a:returnAirEnthalpy
returnEnthalpySp | Return Enthalpy Setpoint | 1 | BTU/lb
returnFan | Return Fan Command | n/a | On/Off
returnFanAlarm | Return Fan Alarm | n/a | On/Off | X | Med | X
returnFanBypass | Return Fan Bypass | n/a | Bypass/Normal
returnFanCurrent | Return Fan Current | 1 | A
returnFanDCVoltage | Return Fan DC Voltage | 1 | V
returnFanEnergy | Return Fan Energy | 1 | kWh
returnFanEnteringPressure | Return Fan Entering Pressure | 2 | inches_of_water
returnFanFault | Return Fan Fault | n/a | Alarm/Normal | X | Med | X
returnFanFrequency | Return Fan Frequency | 1 | Hz
returnFanHandMode | Return Fan Hand/Auto Mode | n/a | Hand/Auto
returnFanLeavingPressure | Return Fan Leaving Pressure | 2 | inches_of_water | X
returnFanMotorSpeed | Return Fan Motor Speed | 0 | rpm | X
returnFanMotorTemp | Return Fan Motor Temperature | 1 | fahrenheit
returnFanOvr | Return Fan Command Override | n/a | On/Off
returnFanPowerReal | Return Fan Power Demand | 1 | kW
returnFanPressureHiAlarm | Return Fan High Pressure Alarm | n/a | Alarm/Normal | X | High | X
returnFanPressureLoAlarm | Return Fan Low Pressure Alarm | n/a | Alarm/Normal | X | High | X
returnFanSpeed | Return Fan Speed | 1 | percent | X
returnFanSpeedFb | Return Fan Speed Feedback | 1 | percent
returnFanSpeedOvr | Return Fan Speed Command Override | 1 | percent
returnFanSpeedSp | Return Fan Speed Setpoint | 1 | percent
returnFanStatus | Return Fan Status | n/a | On/Off | X | Med | X | a:returnFanStatus
returnFanTorque | Return Fan Torque Percent of Maximum | 1 | percent
returnFanVoltage | Return Fan Voltage | 1 | V
returnFlow | Return Airflow | 0 | cfm | X
returnFlowSp | Return Airflow Setpoint | 0 | cfm
returnHumidity | Return Humidity | 1 | percent_relative_humidity | X
returnHumiditySp | Return Humidity Setpoint | 1 | percent_relative_humidity
returnIsoDamper | Return Isolation Damper | n/a | Open/Closed
returnIsoDamperFb | Return Isolation Damper Feedback | 0 | percent
returnIsoDamperOvr | Return Isolation Damper Command Override | n/a | Open/Closed
returnIsoDamperStatus | Return Isolation Damper Status | n/a | Open/Closed
returnPressure | Return Pressure | 2 | inches_of_water | X
returnPressureSp | Return Pressure Setpoint | 2 | inches_of_water
returnSmoke | Return Smoke Alarm | n/a | Alarm/Normal | X | High | X
returnTemp | Return Temperature | 1 | fahrenheit | X |  |  | hs:returnAirTempSensor
returnTempSp | Return Temperature Setpoint | 1 | fahrenheit
secEnteringFlow | Secondary Entering Flow | 0 | gal/min | X
secEnteringFlowSp | Secondary Entering Flow Setpoint | 0 | gal/min
secEnteringPressure | Secondary Entering Pressure | 2 | psi | X
secEnteringTemp | Secondary Entering Temperature | 1 | fahrenheit | X |  |  | hs:chilledWaterEnteringTempSensor OR hs:hotWaterEnteringTempSensor
secLeavingFlow | Secondary Leaving Flow | 0 | gal/min | X
secLeavingFlowMinSp | Secondary Leaving Flow Minimum Setpoint | 0 | gal/min
secLeavingFlowMaxSp | Secondary Leaving Flow Maximum Setpoint | 0 | gal/min
secLeavingFlowSp | Secondary Leaving Flow Setpoint | 0 | gal/min
secLeavingPressure | Secondary Leaving Pressure | 2 | psi | X
secLeavingTemp | Secondary Leaving Temperature | 1 | fahrenheit | X |  |  | hs:chilledWaterLeavingTempSensor/ hs:hotWaterLeavingTempSensor
secLeavingTempSp | Secondary Leaving Temperature Setpoint | 1 | fahrenheit |  |  |  | hs:chilledWaterLeavingTempSp/ hs:hotWaterLeavingTempSp
secPressureDelta | Secondary Pressure Differential | 2 | psi | X |  |  | a:coolingLoopDP/ a:heatingLoopDp
secPressureDeltaSp | Secondary Pressure Differential Setpoint | 2 | psi |  |  |  | a:coolingLoopDPSp/ a:heatingLoopDpSp
secPumpXXX | Secondary Pump Command | n/a | On/Off |  |  |  | a:secondaryChilledWaterPump OR a:secondaryHotWaterPump
secPumpXXXAlarm | Secondary Pump Alarm | n/a | Alarm/Normal | X | Low | X
secPumpXXXBypass | Secondary Pump Bypass | n/a | Bypass/Normal
secPumpXXXCurrent | Secondary Pump Current | 1 | A
secPumpXXXEnergy | Secondary Pump Energy | 1 | kWh
secPumpXXXEnteringPres sure | Secondary Pump Entering Pressure | 2 | psi | X
secPumpXXXFault | Secondary Pump Fault | n/a | Fault/Normal
secPumpXXXFrequency | Secondary Pump Frequency | 1 | Hz
secPumpXXXLeavingPress | Secondary Pump Leaving Pressure | 2 | psi | X
ure
secPumpXXXOvr | Secondary Pump Command Override | n/a | On/Off
secPumpXXXPowerReal | Secondary Pump Power Demand | 2 | kW
secPumpXXXSpeed | Secondary Pump Speed | 0 | percent | X |  |  | a:secondaryChilledWaterPumpSpeed OR a:secondaryHotWaterPumpSpeed
secPumpXXXSpeedFb | Secondary Pump Speed Feedback | 0 | percent
secPumpXXXSpeedOvr | Secondary Pump Speed Override | 0 | percent
secPumpXXXSpeedSp | Secondary Pump Speed Setpoint | 0 | percent
secPumpXXXStatus | Secondary Pump Status | n/a | On/Off | X | Low | X | a:secondaryChilledWaterPumpStatus OR a:secondaryHotWaterPumpStatus
secPumpXXXTorque | Secondary Pump Torque Percent of Maximum | 0 | percent
secTempDelta | Secondary Temperature Differential | 1 | fahrenheit | X
secTempDeltaSp | Secondary Temperature Differential Setpoint | 1 | fahrenheit
shutdownMode | Emergency Shutdown Mode | n/a | On/Off
standbyCoolSp | Zone Standby Cool Setpoint | 1 | fahrenheit
standbyHeatSp | Zone Standby Heat Setpoint | 1 | fahrenheit
stationStatus | JACE station status/ health | n/a | Online/Offline | X | low | x | a:stationHealth
systemActive | System Active | n/a | On/Off | X
systemEnable | System Enable Command | n/a | Available/Unavailable | X |  |  | a:heatingEnable OR a:coolingEnable
systemEnableOvr | System Enable Command Override | n/a | Available/Unavailable
systemEnableSp | System Enable Setpoint | 1 | fahrenheit |  |  |  | a:heatingEnableSp OR a:coolingEnableSp
temp | Temp Points (NOT OAT,CWS,HWS) | 1 | fahrenheit | X |  |  | hs:tempSensor
twrBypassValve | Tower Bypass Valve Command | 0 | percent | X
twrBypassValveFb | Tower Bypass Valve Feedback | 0 | percent
twrBypassValveOvr | Tower Bypass Valve Command Override | 0 | percent
twrDrainValve | Tower Drain Valve | n/a | Open/Closed | X
twrEnteringFlow | Tower Entering Flow | 0 | gal/min | X
twrEnteringPressure | Tower Entering Pressure | 2 | psi | X
twrEnteringTemp | Tower Entering Temperature | 1 | fahrenheit | X
twrFanXXX | Tower Fan Command | n/a | On/Off | X
twrFanXXXAlarm | Tower Fan Alarm | n/a | Alarm/Normal | X | Med | X
twrFanXXXBypass | Tower Fan Bypass | n/a | Bypass/Normal
twrFanXXXCurrent | Tower Fan Current | 1 | A
twrFanXXXEnergy | Tower Fan Energy | 1 | kWh | X
twrFanXXXFault | Tower Fan Fault | n/a | Fault/Normal | X | Med | X
twrFanXXXFrequency | Tower Fan Frequency | 1 | Hz
twrFanXXXOvr | Tower Fan Override Command | n/a | On/Off
twrFanXXXPowerReal | Tower Fan Power Demand | 1 | kW
twrFanXXXSpeed | Tower Fan Speed | 1 | percent | X
twrFanXXXSpeedFb | Tower Fan Speed Feedback | 1 | percent
twrFanXXXSpeedOvr | Tower Fan Speed Override Command | 1 | percent
twrFanXXXSpeedSp | Tower Fan Speed Setpoint | 1 | percent | X
twrFanXXXStage01 | Tower Fan Stage 1 Command | n/a | On/Off | X
twrFanXXXStage02 | Tower Fan Stage 2 Command | n/a | On/Off | X
twrFanXXXStatus | Tower Fan Status | n/a | On/Off | X
twrFanXXXTorque | Tower Fan Torque Percent of Maximum | 1 | percent | X
twrFillValve | Tower Fill (makeup) Valve | n/a | Open/Closed
twrFlowDelta | Tower Flow Differential | 0 | gal/min | X
twrIsoValve | Tower Isolation Valve Command | n/a | Open/Closed
twrIsoValveStatus | Tower Isolation Valve Status | n/a | Open/Closed | X
twrIsoValveOvr | Tower Isolation Valve Command Override | n/a | Open/Closed
twrLeavingFlow | Tower Entering Flow | 0 | gal/min | X
twrLeavingPressure | Tower Leaving Pressure | 2 | psi | X
twrLeavingTemp | Tower Leaving Temperature | 1 | fahrenheit | X
twrLeavingTempHiSp | Tower Leaving Temperature High Setpoint | 1 | fahrenheit
twrLeavingTempLoSp | Tower Leaving Temperature Low Setpoint | 1 | fahrenheit
twrLeavingTempSp | Tower Leaving Temperature Setpoint | 1 | fahrenheit
twrPressureDelta | Tower Pressure Differential | 2 | psi | X
twrSumpLevel | Tower Sump Level | 0 | percent | X
twrSumpLevelFillAlarm | Tower Sump Level Fill Alarm | n/a | Alarm/Normal
twrSumpLevelHiAlarm | Tower Sump Level Hi Alarm | n/a | Alarm/Normal
twrSumpLevelLoAlarm | Tower Sump Level Lo Alarm | n/a | Alarm/Normal
twrSumpTemp | Tower Sump Temperature | 1 | fahrenheit | X
twrTempDelta | Tower Sump Temperature Delta | 1 | fahrenheit | X
unoccupiedCoolSp | Zone Occupied Cool Setpoint | 1 | fahrenheit
unoccupiedHeatSp | Zone Occupied Heat Setpoint | 1 | fahrenheit
voltageLL | Voltage Line to Line (Average) | 1 | V | X
voltageLN | Voltage Line to Neutral (Average) | 1 | V | X
voltagePhaseAB | Voltage Line to Line (Phase AB) | 1 | V | X
voltagePhaseAN | Voltage Line to Neutral (Phase A) | 1 | V | X
voltagePhaseBC | Voltage Line to Line (Phase BC) | 1 | V | X
voltagePhaseBN | Voltage Line to Neutral (Phase B) | 1 | V | X
voltagePhaseCA | Voltage Line to Line (Phase CA) | 1 | V | X
voltagePhaseCN | Voltage Line to Neutral (Phase C) | 1 | V | X
waterValve | Water Valve Command | 0 | percent | X
waterValveFb | Water Valve Feedback | 0 | percent
waterValveMode | Heating/Cooling Changeover Mode | n/a | Heating/Cooling
waterValveOvr | Water Valve Override | 0 | percent
zoneCO | Zone CO | 0 | ppm | X | Low | X
zoneCOSp | Zone CO Setpoint | 0 | ppm
zoneCO2 | Zone CO2 | 0 | ppm | X | Low | X
zoneCO2Sp | Zone CO2 Setpoint | 0 | ppm
zoneCoolSp | Zone Active Cool Setpoint | 1 | fahrenheit
zoneHeatSp | Zone Active Heat Setpoint | 1 | fahrenheit
zoneHumidity | Zone Humidity | 1 | percent_relative_humidity | X | Low | X
zoneHumidityHiSp | Zone Humidity High Setpoint | 1 | percent_relative_humidity
zoneHumidityLoSp | Zone Humidity Low Setpoint | 1 | percent_relative_humidity
zoneHumiditySp | Zone Humidity Setpoint | 1 | percent_relative_humidity
zoneNO2 | Zone NO2 | 0 | ppm | X | Low | X
zoneNO2Sp | Zone NO2 Setpoint | 0 | ppm
zoneOccupiedTempSp | Zone Occupied Temperature Setpoint | 1 | fahrenheit
zonePressureDelta | Zone Pressure to Outside | 2 | inches_of_water
zoneTemp | Zone Temperature | 1 | fahrenheit | X | Low | X | a:spaceTemp
zoneTempAvg | Average of Zone Temperatures | 1 | fahrenheit | X
zoneTempCoolDb | Zone Temperature Cooling Deadband | 1 | fahrenheit
zoneTempDbSp | Zone Temperature Setpoint Deadband | 1 | fahrenheit
zoneTempHeatDb | Zone Temperature Heating Deadband | 1 | fahrenheit
zoneTempMax | Maximum Zone Temperature | 1 | fahrenheit
zoneTempMin | Minimum Zone Temperature | 1 | fahrenheit
zoneTempSp | Zone Temperature Setpoint | 1 | fahrenheit |  |  |  | a:spaceTempSp
zoneTempSpOvr | Zone Temperature Setpoint Override | 1 | fahrenheit
zoneUnoccupiedTempSp | Zone Unoccupied Temperature Setpoint | 1 | fahrenheit
zoneVOC | Zone VOC Level | 0 | unitless | X | Low | X
zoneVOCHiSp | Zone VOC Level Hi Sp (reset) | 0 | unitless
zoneVOCLoSp | Zone VOC Level Lo Sp (reset) | 0 | unitless
zoneVOCSp | Zone VOC Level Setpoint | 0 | unitless