## EBCS Completion Checklist (2)
EBCS Completion Checklist
Completed by **Contractor Name, Phone Number, Date**
Post Integration QA/QC Completed by **Name and Organization, Phone Number, Date**
Station Name and Location |  | Item | Check only if completely met | Comment
Navigation
The EBCS should have a user friendly UI for easy navigation
Equipment Inventory
Equipment Graphics
Equipment Scheduling
History
Alarms
Floorplans 3) Graphics for all BCS controlled e
A complete floor plan should include: 1) An accurate floorplan of all buildings connected to controller with accurate labeling; 2) Zoning and accurate representation of areas served by each piece of equipment; 3) Graphics for all BCS controlled equipment | Floorplan coverage | Unique floorplan for all BCS connected buildings
| Equipment represented in floorplans | All BCS connected equipment included (central and terminal equipment and lighting, etc.) |  |  | Option 1: If it is controlled by the BCS, it should be depicted in the floorplan (see large picture to the right). Option 2: Label all rooms, and in the inventory section, clearly map all central equipment to the zones they serve and all terminal equipment to the rooms they serve.
Graphics in proper locations on floorplan
Equipment linked to graphical displays
| Accurate zoning | Include overview floorplan showing each color-coded zone |  |  | A high level image should display the whole building with color-coded zones. Option 1: Each unique color-coded zones represents the entire space served by a given HVAC equipment (AHU zones, RTU zones, UH zones, etc.). Drill-down floorplan will display at least room numbers and temperatures, and can include depictions of terminal equipment. Option 2: Each unique color-coded zone represents a section of the building and can contain multiple HVAC equipment. Drill-down floorplans need to clearly indicate which HVAC equipment serve the given zone and the specific rooms each HVAC equipment serves. For Option 2, the equipment inventory should indicate which zones all equipment is in, as depicted in the floorplan.
Drill-down floorplans for each zone or building section
Representation of areas served by each piece of equipment is accurate
All rooms should be represented in a zone
In drill-down floorplans, indication of relevant HVAC equipment status (AHUs, RTUs, UHs, etc.) (ON/OFF, supply temp SP, supply temp, Occupied/Unoccupied)
|  | Thermostat locations indicated on the floorplan |  |  | *for Option 2, need to define criteria for creating zones
All zone temperatures displayed and located within the zone
The temperature color scale is applied to each zone
The temperature color scale matches the colors in the specs
| Accurate labeling | All buildings correctly labeled
All equipment correctly labeled
Rooms correctly labeled (if floorplan has details)
Graphics
A complete graphic should include: 1) all important data points and applicable alarms with working and correct links and accurate labels; 2) correct equipment images consistent with the graphic template | Graphic displays for all BCS controlled equipment | Proper buildings
Central equipment (boilers, chillers, AHUs, RTUs, ERVs, MAUs)
Terminal equipment (VAVs, EFs, TFs, UHs, CUHs, FCUs, FTR, Radiant floors, etc.)
Lighting
Other
| Graphics accurately represent equipment, components, and parameters | All central equipment components included and displayed in proper location (pumps, fans, coils, dampers, sensors) |  |  | Refer to 'Components and Parameters' for a sampling of the parameters that should be included for each piece of equipment and each component. All graphics should accurately represent the physical equipment they depict.
All central equipment configurable and nonconfigurable parameters included
All terminal equipment components included (heating/cooling coils, pumps and fans,
All terminal equipment configurable and nonconfigurable parameters included
Equipment and components properly labeled
| In addition to specific parameters, all graphics display: | Schedule (Occupied/Unoccupied)
Manual override
OAT
RH (if applicable)
| Applicable alarms are integrated in the graphics | All relevant alarms included
Site included in RSC state folder
Alarming is routed to EBCS server
Inventory
Inventory | Integration | All equipment on building-level BCS has been integrated to the EBCS
| All central and terminal equipment listed in tabular format | AHU tables display schedule (occupied/unoccupied), status (ON/OFF), supply temperatures, and all VAVs served along with VAV parameters |  |  | All equipment should be included in the inventory along with a snapshot of high level parameters. The best inventory works in categories, with hierarchies when possible. For example, AHUs should each include all associated terminal units (VAVs) and their respective parameters. If a file tree hierarchy navigation is used, the inventory icon can be selected and a drop down list of all categorized equipment displayed, with sub-drop downs for terminal equipment (when pertinent).
RTU tables display schedule (occupied/unoccupied), status (ON/OFF), zone temperature
Terminal equipment tables display schedule (occupied/unoccupied), status (ON/OFF), location, zone temperature, temperature SP, valve status (open/closed), CFM
| Mapping | Clearly indicate zones/spaces served (AHUs/RTUs, etc.)/ rooms served (terminal equipment) |  |  | If floorplan mapping zones are divided into unique zones for each AHU, indicate zones numbers. If mapping is done in sections not specific to each AHU, list rooms served by each AHU.
All equipment should be represented in a zone (from floorplan)
| Links | All equipment linked to graphical displays
There are no missing links
All the links are working properly
The links correspond to the correct building/equipment/data point
Scheduling should be set up for all the applicable equipment and with all the appropriate scheduling options | All relevant equipment included in scheduling | Daily Schedule: AHUs, RTUs, ERVs, UHs, EFs, FTR, Lighting etc.
| All scheduling options included for all relevant equipment | Holiday scheduling
Special events scheduling
Logic/ Sequencing | Logic/Sequencing | Include records of sequencing changes if edited by contractor.
IC JACE Graphics | Graphics | IC Jace must have EBCS graphics and be capable of user navigation
History | History | Historical logs of all compiled data viewable up to 14 days
Alarms | Alarms and routing to server | Logical equipment alarms need to be placed and route to the server
Additional notes |  | All pages show correct RSC shield in background
IP Address (provide information in Column D)
JACE IP address | JACE IP address
JACE Model and Niagara Version | JACE Model and Niagara Version
Station Pass Phrase | Station Pass Phrase
Admin/super user Use name and passwords | Admin/super user Use name and passwords

## EBCS Completion Checklist
EBCS Completion Checklist
Completed by **Contractor Name, Phone Number, Date**
Post Integration QA/QC Completed by **Name and Organization, Phone Number, Date**
Station Name and Location |  | Item | Check only if completely met | Comment
Navigation
The EBCS should have a user friendly UI for easy navigation | Include working links spanning the top of all pages or a file tree hierarchy containing the following items: | Floorplans
Equipment Inventory
Equipment Graphics
Equipment Scheduling
History
Alarms
Floorplans 3) Graphics for all BCS controlled e
A complete floor plan should include: 1) An accurate floorplan of all buildings connected to controller with accurate labeling; 2) Zoning and accurate representation of areas served by each piece of equipment; 3) Graphics for all BCS controlled equipment | Floorplan coverage | Unique floorplan for all BCS connected buildings
| Equipment represented in floorplans | All BCS connected equipment included (central and terminal equipment and lighting, etc.) |  |  | Option 1: If it is controlled by the BCS, it should be depicted in the floorplan (see large picture to the right). Option 2: Label all rooms, and in the inventory section, clearly map all central equipment to the zones they serve and all terminal equipment to the rooms they serve.
Graphics in proper locations on floorplan
Equipment linked to graphical displays
| Accurate zoning | Include overview floorplan showing each color-coded zone |  |  | A high level image should display the whole building with color-coded zones. Option 1: Each unique color-coded zones represents the entire space served by a given HVAC equipment (AHU zones, RTU zones, UH zones, etc.). Drill-down floorplan will display at least room numbers and temperatures, and can include depictions of terminal equipment. Option 2: Each unique color-coded zone represents a section of the building and can contain multiple HVAC equipment. Drill-down floorplans need to clearly indicate which HVAC equipment serve the given zone and the specific rooms each HVAC equipment serves. For Option 2, the equipment inventory should indicate which zones all equipment is in, as depicted in the floorplan.
Drill-down floorplans for each zone or building section
Representation of areas served by each piece of equipment is accurate
All rooms should be represented in a zone
In drill-down floorplans, indication of relevant HVAC equipment status (AHUs, RTUs, UHs, etc.) (ON/OFF, supply temp SP, supply temp, Occupied/Unoccupied)
|  | Thermostat locations indicated on the floorplan |  |  | *for Option 2, need to define criteria for creating zones
All zone temperatures displayed and located within the zone
The temperature color scale is applied to each zone
The temperature color scale matches the colors in the specs
| Accurate labeling | All buildings correctly labeled
All equipment correctly labeled
Rooms correctly labeled (if floorplan has details)
Graphics
A complete graphic should include: 1) all important data points and applicable alarms with working and correct links and accurate labels; 2) correct equipment images consistent with the graphic template | Graphic displays for all BCS controlled equipment | Proper buildings
Central equipment (boilers, chillers, AHUs, RTUs, ERVs, MAUs)
Terminal equipment (VAVs, EFs, TFs, UHs, CUHs, FCUs, FTR, Radiant floors, etc.)
Lighting
Other
| Graphics accurately represent equipment, components, and parameters | All central equipment components included and displayed in proper location (pumps, fans, coils, dampers, sensors) |  |  | Refer to 'Components and Parameters' for a sampling of the parameters that should be included for each piece of equipment and each component. All graphics should accurately represent the physical equipment they depict.
All central equipment configurable and nonconfigurable parameters included
All terminal equipment components included (heating/cooling coils, pumps and fans,
All terminal equipment configurable and nonconfigurable parameters included
Equipment and components properly labeled
| In addition to specific parameters, all graphics display: | Schedule (Occupied/Unoccupied)
Manual override
OAT
RH (if applicable)
| Applicable alarms are integrated in the graphics | All relevant alarms included
Site included in RSC state folder
Alarming is routed to EBCS server
Inventory
Inventory | Integration | All equipment on building-level BCS has been integrated to the EBCS
| All central and terminal equipment listed in tabular format | AHU tables display schedule (occupied/unoccupied), status (ON/OFF), supply temperatures, and all VAVs served along with VAV parameters |  |  | All equipment should be included in the inventory along with a snapshot of high level parameters. The best inventory works in categories, with hierarchies when possible. For example, AHUs should each include all associated terminal units (VAVs) and their respective parameters. If a file tree hierarchy navigation is used, the inventory icon can be selected and a drop down list of all categorized equipment displayed, with sub-drop downs for terminal equipment (when pertinent).
RTU tables display schedule (occupied/unoccupied), status (ON/OFF), zone temperature
Terminal equipment tables display schedule (occupied/unoccupied), status (ON/OFF), location, zone temperature, temperature SP, valve status (open/closed), CFM
| Mapping | Clearly indicate zones/spaces served (AHUs/RTUs, etc.)/ rooms served (terminal equipment) |  |  | If floorplan mapping zones are divided into unique zones for each AHU, indicate zones numbers. If mapping is done in sections not specific to each AHU, list rooms served by each AHU.
All equipment should be represented in a zone (from floorplan)
| Links | All equipment linked to graphical displays
There are no missing links
All the links are working properly
The links correspond to the correct building/equipment/data point
Scheduling should be set up for all the applicable equipment and with all the appropriate scheduling options | All relevant equipment included in scheduling | Daily Schedule: AHUs, RTUs, ERVs, UHs, EFs, FTR, Lighting etc.
| All scheduling options included for all relevant equipment | Holiday scheduling
Special events scheduling
Logic/ Sequencing | Logic/Sequencing | Include records of sequencing changes if edited by contractor.
IC JACE Graphics | Graphics | IC Jace must have EBCS graphics and be capable of user navigation
History | History | Historical logs of all compiled data viewable up to 14 days
Alarms | Alarms and routing to server | Logical equipment alarms need to be placed and route to the server
Additional notes |  | All pages show correct RSC shield in background
IP Address (provide information in Column D)
JACE IP address | JACE IP address
JACE Model and Niagara Version | JACE Model and Niagara Version
Station Pass Phrase | Station Pass Phrase
Admin/super user Use name and passwords | Admin/super user Use name and passwords

## Identified issues (hidden)
Floorplans Incomplete | 18
Graphics Inaccurate/ Incomplete | 14
Graphics Missing Information | 11
Links missing/ not Working | 10
Equipment Missing from Graphics | 9
Wrong RSC in Background | 9
No Equipment Schedules | 7
No Holiday Schedules | 7
Missing Configurable Parameters | 5
Equipment Missing from Floorplans | 5
Equipment Missing from Schedules | 5
Alarm service not included at RSC99th state folder | 5
Building Name Mislabeled | 5
Equipment Mislabeled | 4
No OAT in Graphics | 4
Equipment not Integrated | 3
Site Improperly Integrated | 3
Alarming not routed to EBCS server | 2
No OMS Graphic | 2
Equipment not Agreeing with Mech Drawings | 1
Graphics Missing Information | 1
Data Points not Mapped | 1
No Power Meter integrated to JACE | 1
Points Editable that Shouldn't be | 1
Sensors and Points Missing | 1